## README
Tamil Nadu – 9 balancing areas, inter-area transmission (end of FY2025-26)
PyPSA network. Load with: n = pypsa.Network(); n.import_from_excel('TN_9BA_interarea_pypsa_FY2025-26.xlsx') (tested with PyPSA 1.4). This README and the 'circuits' sheet are ignored on import.
What is in it
buses: the 9 TN balancing areas (from TN_district-regions.geojson); x/y = map anchor (lon/lat); v_nom = 400 kV reference. Extra columns: within_area_mw / within_area_circuits = sum of ratings of circuits with both ends in the area (not used by PyPSA).
lines (active): 18 area pairs, one equivalent branch each. s_nom = sum of circuit ratings in MW (120,072 MW in total). x, r = parallel combination of the circuit impedances, in ohm referred to 400 kV; b = sum of circuit susceptances in siemens at 400 kV. length = mean circuit length (km, informational). Extra columns: s_nom_n1 (sum minus largest circuit; 89,095 MW in total), largest_circuit_mw, n_circuits, circuits_by_kv, mw_by_kv, line_ids.
links (inactive): the same pairs as a transport model (p_nom = s_nom, p_min_pu = -1). To use the transport model instead of DC power flow: n.lines['active'] = False; n.links['active'] = True.
circuits: every circuit crossing an area boundary, with endpoints, conductor, length, per-unit and ohmic parameters, rating, limit type and source. Use it to rebuild or re-aggregate.
No generators, loads, storage or snapshots are included – add your own.
How the numbers were made
Circuit rating = min(thermal, 30° angular-stability limit). Thermal: ACSR Moose 1,068 MW per 400 kV twin circuit at 40 °C ambient / 75 °C conductor (Pentayya et al., 'Line Loadability in Indian Perspective', NPSC 2012), scaled by sqrt(R_Moose/R) per conductor, 0.95 power factor. Stability: P = 100·sin30°/(x_pu·L). R, X, B from the line-parameter table of the SRLDC Compendium of SR Transmission Elements 2023 (pu/km on 100 MVA, re-based to the operating voltage).
Per-unit impedances on a common 100 MVA base are voltage-independent, so 765 kV and 230 kV circuits are combined with 400 kV ones by converting pu to ohm at 400 kV (Z_base = 1,600 ohm). Transformers between voltage levels are not modelled.
Network: SRLDC Compendium of SR Transmission Elements 2023 (as of 31-05-2023) + new lines and LILO re-arrangements in the SR Annual Compendiums 2023-24, 2024-25 and 2025-26. Substations placed with OpenStreetMap and assigned to areas by polygon.
Caveats – read before using s_nom as a transfer limit
1. s_nom is a sum of circuit ratings, not a transfer capability. On the comparable S1→(S2+S3) corridor the sum of ratings is roughly 3× Grid-India's TTC (11,300 MW in FY2025-26), because flows split by impedance, N-1 security applies and 400/230 kV transformers bind (Kalivandapattu, Pugalur). Calibrate s_max_pu (e.g. 0.3–0.7) or derive NTCs before using these as limits.
2. The equivalent x of each pair ignores impedance inside the areas, so PTDFs from this 9-node model are approximate. For accurate flows, use the nodal network (tn_lines.csv) and aggregate afterwards.
3. 230 kV TANTRANSCO lines are as of May 2023; 230 kV additions since then are not itemised in any SRLDC source. 400 kV and above are complete to March 2026.
4. Excluded: one 230 kV underground cable without parameters (Kadaperi–Alandur CMRL, see 'circuits', rated = FALSE); Sholinganallur–Tharamani 400 kV (isolator open as of March 2026). 110 kV and below are not included.
5. Transmission reliability margin per Grid-India: largest unit in the importing area or 2% of peak demand – subtract it if you derive NTCs.

## lines
name | bus0 | bus1 | x | r | b | s_nom | length | carrier | s_nom_n1 | largest_circuit_mw | n_circuits | n_circuits_rated | circuits_by_kv | mw_by_kv | line_ids
Madurai–Tirunelveli | Madurai | Tirunelveli | 2.4215 | 0.2499 | 0.0060768 | 17462 | 113.9 | AC | 15418 | 2044 | 23 | 23 | 400 kV ×8; 230 kV ×15 | 400 kV: 13482; 230 kV: 3980 | L0034 L0035 L0078 L0079 L0102 L0103 L0106 L0107 L0188 L0195 L0215 L0216 L0218 L0221 L0223 L0284 L0285 L0286 L0312 L0316 L0425 L0428 L0495
Vellore–Villupuram | Vellore | Villupuram | 4.5613 | 0.264 | 0.0078282 | 14070 | 160.7 | AC | 8832 | 5238 | 6 | 6 | 765 kV ×2; 400 kV ×2; 230 kV ×2 | 765 kV: 10476; 400 kV: 3074; 230 kV: 520 | L0003 L0004 L0199 L0454 L0529 L0545
Madurai–Trichy | Madurai | Trichy | 4.0957 | 0.4224 | 0.0042992 | 11432 | 110.9 | AC | 9388 | 2044 | 12 | 12 | 400 kV ×7; 230 kV ×5 | 400 kV: 10122; 230 kV: 1310 | L0032 L0033 L0083 L0084 L0108 L0109 L0110 L0169 L0292 L0293 L0301 L0435
Erode–Vellore | Erode | Vellore | 2.8726 | 0.2158 | 0.0023539 | 11266 | 88.8 | AC | 9222 | 2044 | 10 | 10 | 400 kV ×6; 230 kV ×4 | 400 kV: 10206; 230 kV: 1060 | L0063 L0064 L0065 L0066 L0118 L0119 L0249 L0360 L0373 L0443
Trichy–Villupuram | Trichy | Villupuram | 5.5651 | 0.6148 | 0.0056243 | 9612 | 147.4 | AC | 7894 | 1718 | 11 | 11 | 400 kV ×7; 230 kV ×4 | 400 kV: 8562; 230 kV: 1050 | L0052 L0060 L0061 L0085 L0086 L0125 L0231 L0266 L0267 L0465 L0518
Chennai North–Villupuram | Chennai North | Villupuram | 9.5062 | 0.457 | 0.009062 | 8416 | 272.5 | AC | 4208 | 4208 | 2 | 2 | 765 kV ×2 | 765 kV: 8416 | L0525 L0527
Chennai North–Chennai South | Chennai North | Chennai South | 1.9446 | 0.2683 | 0.0023128 | 8282 | 60.3 | AC | 7250 | 1032 | 15 | 14 | 400 kV ×6; 230 kV ×9 | 400 kV: 6192; 230 kV: 2090 | L0025 L0026 L0093 L0094 L0129 L0273 L0275 L0280 L0338 L0341 L0388 L0462 L0463 L0470 L0544
Coimbatore–Vellore | Coimbatore | Vellore | 9.749 | 0.5655 | 0.0070918 | 8204 | 258 | AC | 6541 | 1663 | 6 | 6 | 400 kV ×6 | 400 kV: 8204 | L0058 L0059 L0121 L0122 L0123 L0124
Coimbatore–Erode | Coimbatore | Erode | 4.6355 | 0.656 | 0.0024265 | 6224 | 83.8 | AC | 5192 | 1032 | 12 | 12 | 400 kV ×4; 230 kV ×8 | 400 kV: 4094; 230 kV: 2130 | L0067 L0068 L0116 L0117 L0202 L0206 L0237 L0255 L0257 L0305 L0309 L0421
Chennai South–Villupuram | Chennai South | Villupuram | 9.1087 | 1.2342 | 0.0024238 | 5247 | 124.4 | AC | 3539 | 1708 | 9 | 9 | 400 kV ×2; 230 kV ×7 | 400 kV: 3407; 230 kV: 1840 | L0099 L0147 L0148 L0168 L0197 L0198 L0505 L0506 L0517
Coimbatore–Trichy | Coimbatore | Trichy | 4.6827 | 0.2716 | 0.00033901 | 4088 | 37 | AC | 2044 | 2044 | 2 | 2 | 400 kV ×2 | 400 kV: 4088 | L0520 L0522
Coimbatore–Madurai | Coimbatore | Madurai | 14.2239 | 1.505 | 0.0018651 | 3339 | 141.2 | AC | 2307 | 1032 | 4 | 4 | 400 kV ×3; 230 kV ×1 | 400 kV: 3079; 230 kV: 260 | L0038 L0095 L0096 L0386
Chennai North–Vellore | Chennai North | Vellore | 11.9616 | 1.4417 | 0.00097511 | 2594 | 90.2 | AC | 1562 | 1032 | 4 | 4 | 400 kV ×2; 230 kV ×2 | 400 kV: 2064; 230 kV: 530 | L0014 L0015 L0175 L0366
Chennai South–Vellore | Chennai South | Vellore | 11.2747 | 1.4286 | 0.00095873 | 2584 | 83 | AC | 1552 | 1032 | 4 | 4 | 400 kV ×2; 230 kV ×2 | 400 kV: 2064; 230 kV: 520 | L0023 L0024 L0291 L0479
Erode–Villupuram | Erode | Villupuram | 23.1628 | 2.5506 | 0.0013152 | 2290 | 148 | AC | 1275 | 1015 | 3 | 3 | 400 kV ×2; 230 kV ×1 | 400 kV: 2030; 230 kV: 260 | L0069 L0070 L0229
Coimbatore–Tirunelveli | Coimbatore | Tirunelveli | 40.7676 | 3.816 | 0.0019941 | 1962 | 265 | AC | 981 | 981 | 2 | 2 | 400 kV ×2 | 400 kV: 1962 | L0043 L0044
Tirunelveli–Vellore | Tirunelveli | Vellore | 47.0767 | 2.2631 | 0.0033544 | 1700 | 369 | AC | 850 | 850 | 2 | 2 | 400 kV ×2 | 400 kV: 1700 | L0005 L0006
Erode–Trichy | Erode | Trichy | 9.347 | 1.7529 | 0.00023086 | 1300 | 47.6 | AC | 1040 | 260 | 5 | 5 | 230 kV ×5 | 230 kV: 1300 | L0161 L0187 L0422 L0423 L0437

## links
name | bus0 | bus1 | carrier | active | p_nom | p_min_pu | p_nom_n1 | line_ids
Madurai–Tirunelveli | Madurai | Tirunelveli | AC | FALSE | 17462 | -1 | 15418 | L0034 L0035 L0078 L0079 L0102 L0103 L0106 L0107 L0188 L0195 L0215 L0216 L0218 L0221 L0223 L0284 L0285 L0286 L0312 L0316 L0425 L0428 L0495
Vellore–Villupuram | Vellore | Villupuram | AC | FALSE | 14070 | -1 | 8832 | L0003 L0004 L0199 L0454 L0529 L0545
Madurai–Trichy | Madurai | Trichy | AC | FALSE | 11432 | -1 | 9388 | L0032 L0033 L0083 L0084 L0108 L0109 L0110 L0169 L0292 L0293 L0301 L0435
Erode–Vellore | Erode | Vellore | AC | FALSE | 11266 | -1 | 9222 | L0063 L0064 L0065 L0066 L0118 L0119 L0249 L0360 L0373 L0443
Trichy–Villupuram | Trichy | Villupuram | AC | FALSE | 9612 | -1 | 7894 | L0052 L0060 L0061 L0085 L0086 L0125 L0231 L0266 L0267 L0465 L0518
Chennai North–Villupuram | Chennai North | Villupuram | AC | FALSE | 8416 | -1 | 4208 | L0525 L0527
Chennai North–Chennai South | Chennai North | Chennai South | AC | FALSE | 8282 | -1 | 7250 | L0025 L0026 L0093 L0094 L0129 L0273 L0275 L0280 L0338 L0341 L0388 L0462 L0463 L0470 L0544
Coimbatore–Vellore | Coimbatore | Vellore | AC | FALSE | 8204 | -1 | 6541 | L0058 L0059 L0121 L0122 L0123 L0124
Coimbatore–Erode | Coimbatore | Erode | AC | FALSE | 6224 | -1 | 5192 | L0067 L0068 L0116 L0117 L0202 L0206 L0237 L0255 L0257 L0305 L0309 L0421
Chennai South–Villupuram | Chennai South | Villupuram | AC | FALSE | 5247 | -1 | 3539 | L0099 L0147 L0148 L0168 L0197 L0198 L0505 L0506 L0517
Coimbatore–Trichy | Coimbatore | Trichy | AC | FALSE | 4088 | -1 | 2044 | L0520 L0522
Coimbatore–Madurai | Coimbatore | Madurai | AC | FALSE | 3339 | -1 | 2307 | L0038 L0095 L0096 L0386
Chennai North–Vellore | Chennai North | Vellore | AC | FALSE | 2594 | -1 | 1562 | L0014 L0015 L0175 L0366
Chennai South–Vellore | Chennai South | Vellore | AC | FALSE | 2584 | -1 | 1552 | L0023 L0024 L0291 L0479
Erode–Villupuram | Erode | Villupuram | AC | FALSE | 2290 | -1 | 1275 | L0069 L0070 L0229
Coimbatore–Tirunelveli | Coimbatore | Tirunelveli | AC | FALSE | 1962 | -1 | 981 | L0043 L0044
Tirunelveli–Vellore | Tirunelveli | Vellore | AC | FALSE | 1700 | -1 | 850 | L0005 L0006
Erode–Trichy | Erode | Trichy | AC | FALSE | 1300 | -1 | 1040 | L0161 L0187 L0422 L0423 L0437

## buses
name | v_nom | x | y | within_area_mw | within_area_circuits
Tirunelveli | 400 | 77.721 | 8.947 | 57993 | 85
Villupuram | 400 | 79.265 | 12.006 | 17444 | 30
Chennai North | 400 | 79.929 | 13.201 | 29276 | 63
Coimbatore | 400 | 77.064 | 10.956 | 30706 | 58
Madurai | 400 | 78.114 | 9.939 | 11221 | 26
Chennai South | 400 | 79.918 | 12.656 | 11289 | 36
Trichy | 400 | 78.947 | 10.752 | 8452 | 27
Vellore | 400 | 78.438 | 12.473 | 8070 | 21
Erode | 400 | 77.852 | 11.495 | 7340 | 28

## circuits
line_id | ba_from | ba_to | frm | to | from_name | to_name | kv | kv_design | type | circuit | tower | conductor | length_km | capacity_mw | limit | thermal_mw | stability_mw | r_pu_km | x_pu_km | b_pu_km | r_ohm | x_ohm | b_siemens | rated | owner | status | confidence | source | note | cap_note
L0025 | Chennai North | Chennai South | KALIVANTHAPATU | VALLUR | Kalivandapattu 400/230 | Vallur TPS (NTECL) 400 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 134 | 1032 | thermal | 1032 | 1940 | 1.8e-05 | 0.0001923 | 0.00602 | 3.8592 | 41.2291 | 0.00050418 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 179
L0026 | Chennai North | Chennai South | KALIVANTHAPATU | VALLUR | Kalivandapattu 400/230 | Vallur TPS (NTECL) 400 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 134 | 1032 | thermal | 1032 | 1940 | 1.8e-05 | 0.0001923 | 0.00602 | 3.8592 | 41.2291 | 0.00050418 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 180
L0093 | Chennai North | Chennai South | ALAMATHI | S V CHATHRAM | Alamathi 400/230 | Sunguvarchatram 400/230 | 400 | 400 | AC | 1 | M/C | TWIN ACSR MOOSE | 47 | 1032 | thermal | 1032 | 5532 | 1.8e-05 | 0.0001923 | 0.00602 | 1.3536 | 14.461 | 0.00017684 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 339
L0094 | Chennai North | Chennai South | ALAMATHI | S V CHATHRAM | Alamathi 400/230 | Sunguvarchatram 400/230 | 400 | 400 | AC | 2 | M/C | TWIN ACSR MOOSE | 47 | 1032 | thermal | 1032 | 5532 | 1.8e-05 | 0.0001923 | 0.00602 | 1.3536 | 14.461 | 0.00017684 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 340
L0129 | Chennai North | Chennai South | S V CHATHRAM | NCTPS STG2 | Sunguvarchatram 400/230 | North Chennai TPS St-II 400 | 400 | 400 | AC | 1 | M/C | TWIN ACSR MOOSE | 95 | 1032 | thermal | 1032 | 2737 | 1.8e-05 | 0.0001923 | 0.00602 | 2.736 | 29.2296 | 0.00035744 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 377
L0544 | Chennai North | Chennai South | S V CHATHRAM | ENNORE SEZ | Sunguvarchatram 400/230 | Ennore SEZ 400 | 400 | 400 | AC | 1 | M/C | TWIN ACSR MOOSE | 77.821 | 1032 | thermal | 1032 | 3341 | 1.8e-05 | 0.0001923 | 0.00602 | 2.2412 | 23.944 | 0.0002928 | TRUE | TANTRANSCO | in service | high | SR Annual Compendium 2025-26 (SRLDC), Table 58 (LILO), 27-02-2026 | LILO section; which S.V.Chathram–NCTPS circuit was LILO'd is assumed (ckt-2)
L0273 | Chennai North | Chennai South | KADAPERI | ALANDUR | Kadaperi (Tambaram) | Alandur (CMRL) | 230 | 230 | AC | 1 | S/C | 1200SQMM UGC | 12 | [10 empty] | FALSE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 611 |  | underground cable; no tabulated parameters – capacity not computed
L0275 | Chennai North | Chennai South | KADAPERI | PORUR | Kadaperi (Tambaram) | Porur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 9 | 260 | thermal | 260 | 7361 | 0.00014154 | 0.00075473 | 0.001552 | 2.0382 | 10.8681 | 8.7301e-06 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 613 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0280 | Chennai North | Chennai South | KALIVANTHAPATU | TARAMANI | Kalivandapattu 400/230 | Tharamani 400/230 GIS | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 45 | 260 | thermal | 260 | 1472 | 0.00014154 | 0.00075473 | 0.001552 | 10.1909 | 54.3405 | 4.3651e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 618 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0338 | Chennai North | Chennai South | KORATTUR | SRIPERUMBUDUR | Korattur 400/230/110 | Sriperumbudur 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 30 | 260 | thermal | 260 | 2208 | 0.00014154 | 0.00075473 | 0.001552 | 6.7939 | 36.227 | 2.91e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 676
L0341 | Chennai North | Chennai South | KOYAMBEDU | SRIPERUMBUDUR | Koyambedu | Sriperumbudur 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + 1200SQMM UGC | 46 | 260 | thermal | 260 | 1440 | 0.00014154 | 0.00075473 | 0.001552 | 10.4174 | 55.548 | 4.4621e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 679 |  | underground cable; mixed sections: weakest (highest-resistance) conductor used for whole line; cable section present – overhead parameters used, cable rating may be lower
L0388 | Chennai North | Chennai South | NCTPS STG1 | SRIPERUMBUDUR | North Chennai TPS St-I 230 | Sriperumbudur 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 73 | 260 | thermal | 260 | 908 | 0.00014154 | 0.00075473 | 0.001552 | 16.5319 | 88.1523 | 7.0811e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 726
L0462 | Chennai North | Chennai South | SRIPERUMBUDUR | SURYA DEV | Sriperumbudur 400/230 | Surya Dev (industrial) | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 54 | 260 | thermal | 260 | 1227 | 0.00014154 | 0.00075473 | 0.001552 | 12.2291 | 65.2086 | 5.2381e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 800 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0463 | Chennai North | Chennai South | SRIPERUMBUDUR | TARAMANI | Sriperumbudur 400/230 | Tharamani 400/230 GIS | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 35 | 260 | thermal | 260 | 1893 | 0.00014154 | 0.00075473 | 0.001552 | 7.9263 | 42.2648 | 3.3951e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 801
L0470 | Chennai North | Chennai South | TARAMANI | KITZ | Tharamani 400/230 GIS | KITZ (Sholinganallur) | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 18 | 270 | thermal | 270 | 3693 | 0.00013175 | 0.00075208 | 0.0015411 | 3.7944 | 21.6598 | 1.7337e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 808 |  | S/C parameters used (D/C not tabulated)
L0014 | Chennai North | Vellore | ALAMATHI | THIRUVALAM-TN | Alamathi 400/230 | Thiruvalam (TN) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 112 | 1032 | thermal | 1032 | 2322 | 1.8e-05 | 0.0001923 | 0.00602 | 3.2256 | 34.4602 | 0.0004214 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 128
L0015 | Chennai North | Vellore | ALAMATHI | THIRUVALAM-TN | Alamathi 400/230 | Thiruvalam (TN) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 112 | 1032 | thermal | 1032 | 2322 | 1.8e-05 | 0.0001923 | 0.00602 | 3.2256 | 34.4602 | 0.0004214 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 129
L0175 | Chennai North | Vellore | ALAMATHI | MOSUR | Alamathi 400/230 | Mosur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 52 | 260 | thermal | 260 | 1274 | 0.00014154 | 0.00075473 | 0.001552 | 11.7762 | 62.7934 | 5.0441e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 513 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0366 | Chennai North | Vellore | MOSUR | ATHIPATU | Mosur | Athipattu 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 85 | 270 | thermal | 270 | 782 | 0.00013175 | 0.00075208 | 0.0015411 | 17.9181 | 102.2823 | 8.1871e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 704
L0525 | Chennai North | Villupuram | NORTH CHENNAI PS | ARIYALUR | North Chennai 765 kV PS | Ariyalur 765/400 | 765 | 765 | AC | 1 | D/C | HEXA ACSR ZEBRA | 272.54 | 4208 | stability (30°) | 5238 | 4208 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.91399 | 19.0124 | 0.004531 | TRUE | TANTRANSCO | in service | high | SR Annual Compendium 2023-24 (SRLDC), Table 33 #26, 06-01-2024
L0527 | Chennai North | Villupuram | NORTH CHENNAI PS | ARIYALUR | North Chennai 765 kV PS | Ariyalur 765/400 | 765 | 765 | AC | 2 | D/C | HEXA ACSR ZEBRA | 272.54 | 4208 | stability (30°) | 5238 | 4208 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.91399 | 19.0124 | 0.004531 | TRUE | TANTRANSCO | in service | high | SR Annual Compendium 2023-24 (SRLDC), Table 33 #25, 18-01-2024
L0023 | Chennai South | Vellore | KALIVANTHAPATU | THIRUVALAM-PG | Kalivandapattu 400/230 | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 114 | 1032 | thermal | 1032 | 2281 | 1.8e-05 | 0.0001923 | 0.00602 | 3.2832 | 35.0755 | 0.00042892 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 177
L0024 | Chennai South | Vellore | KALIVANTHAPATU | THIRUVALAM-PG | Kalivandapattu 400/230 | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 114 | 1032 | thermal | 1032 | 2281 | 1.8e-05 | 0.0001923 | 0.00602 | 3.2832 | 35.0755 | 0.00042892 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 178
L0291 | Chennai South | Vellore | KANCHIPURAM | THIRUVALAM-TN | Kanchipuram | Thiruvalam (TN) 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 52 | 260 | thermal | 260 | 1274 | 0.00014154 | 0.00075473 | 0.001552 | 11.7762 | 62.7934 | 5.0441e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 629
L0479 | Chennai South | Vellore | THIRUVALAM 230/110 | KANCHIPURAM | Thiruvalam (TN) 230/110 | Kanchipuram | 230 | 230 | AC | 1 | D/C | SINGLE ACSR KUNDAH | 52 | 260 | thermal | 260 | 1274 | 0.00014154 | 0.00075473 | 0.001552 | 11.7762 | 62.7934 | 5.0441e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 817 |  | S/C parameters used (D/C not tabulated)
L0099 | Chennai South | Villupuram | KALIVANTHAPATU | ARIYALUR | Kalivandapattu 400/230 | Ariyalur 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 186 | 1699 | stability (30°) | 2044 | 1699 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7311 | 47.0803 | 0.00085211 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 345
L0517 | Chennai South | Villupuram | KALIVANTHAPATU | ARIYALUR | Kalivandapattu 400/230 | Ariyalur 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 185 | 1708 | stability (30°) | 2044 | 1708 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7164 | 46.8272 | 0.00084753 | TRUE | TANTRANSCO | in service | high | SR Annual Compendium 2023-24 (SRLDC), Table 34 #17 (LILO), 12-02-2024
L0147 | Chennai South | Villupuram | ARANI | BHAVINI | Arani | BHAVINI PFBR Kalpakkam | 230 | 230 | AC | 1 | D/C | SINGLE AAAC ZEBRA | 106 | 260 | thermal | 260 | 625 | 0.00014154 | 0.00075473 | 0.001552 | 24.0052 | 128.002 | 0.00010282 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 485 |  | S/C parameters used (D/C not tabulated)
L0148 | Chennai South | Villupuram | ARANI | BHAVINI | Arani | BHAVINI PFBR Kalpakkam | 230 | 230 | AC | 2 | D/C | SINGLE AAAC ZEBRA | 106 | 260 | thermal | 260 | 625 | 0.00014154 | 0.00075473 | 0.001552 | 24.0052 | 128.002 | 0.00010282 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 486 |  | S/C parameters used (D/C not tabulated)
L0168 | Chennai South | Villupuram | ACHARAPAKKAM | VILLUPURAM | Acharapakkam | Villupuram | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 72 | 260 | thermal | 260 | 920 | 0.00014154 | 0.00075473 | 0.001552 | 16.3054 | 86.9448 | 6.9841e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 506
L0197 | Chennai South | Villupuram | ARANI | ECHUR | Arani | Echur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 46 | 260 | thermal | 260 | 1440 | 0.00014154 | 0.00075473 | 0.001552 | 10.4174 | 55.548 | 4.4621e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 535 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0198 | Chennai South | Villupuram | ARANI | KANCHIPURAM | Arani | Kanchipuram | 230 | 230 | AC | 2 | S/C | SINGLE ACSR KUNDAH | 63 | 260 | thermal | 260 | 1052 | 0.00014154 | 0.00075473 | 0.001552 | 14.2673 | 76.0767 | 6.1111e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 536
L0505 | Chennai South | Villupuram | VEERAPURAM | CUDDALORE | Veerapuram | Cuddalore | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 178 | 270 | thermal | 270 | 373 | 0.00013175 | 0.00075208 | 0.0015411 | 37.5225 | 214.1911 | 0.00017145 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 843 |  | S/C parameters used (D/C not tabulated)
L0506 | Chennai South | Villupuram | VEERAPURAM | CUDDALORE | Veerapuram | Cuddalore | 230 | 230 | AC | 2 | D/C | SINGLE ACSR ZEBRA | 178 | 270 | thermal | 270 | 373 | 0.00013175 | 0.00075208 | 0.0015411 | 37.5225 | 214.1911 | 0.00017145 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 844 |  | S/C parameters used (D/C not tabulated)
L0067 | Coimbatore | Erode | SALEM-PG | MYWADI | Salem (PG) 400/230 | Udumalpet / Mywadi (PG) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 150 | 1015 | thermal | 1015 | 1606 | 1.862e-05 | 0.0002075 | 0.00555 | 4.4688 | 49.8 | 0.00052031 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 274
L0068 | Coimbatore | Erode | SALEM-PG | MYWADI | Salem (PG) 400/230 | Udumalpet / Mywadi (PG) 400/230 | 400 | 400 | AC | 2 | S/C | TWIN ACSR MOOSE | 150 | 1015 | thermal | 1015 | 1606 | 1.862e-05 | 0.0002075 | 0.00555 | 4.4688 | 49.8 | 0.00052031 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 275
L0116 | Coimbatore | Erode | MTPS-3 | KARAMADAI | Mettur TPS St-III 400/230 | Karamadai 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 126 | 1032 | thermal | 1032 | 2064 | 1.8e-05 | 0.0001923 | 0.00602 | 3.6288 | 38.7677 | 0.00047408 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 364
L0117 | Coimbatore | Erode | MTPS-3 | KARAMADAI | Mettur TPS St-III 400/230 | Karamadai 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 126 | 1032 | thermal | 1032 | 2064 | 1.8e-05 | 0.0001923 | 0.00602 | 3.6288 | 38.7677 | 0.00047408 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 365
L0202 | Coimbatore | Erode | ARASUR | GOBI | Arasur (TN) | Gobichettipalayam | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 80 | 260 | thermal | 260 | 828 | 0.00014154 | 0.00075473 | 0.001552 | 18.1172 | 96.6053 | 7.7601e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 540
L0206 | Coimbatore | Erode | ARASUR | SHENBAGAPUDUR | Arasur (TN) | Shenbagapudur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 66 | 270 | thermal | 270 | 1007 | 0.00013175 | 0.00075208 | 0.0015411 | 13.9128 | 79.4192 | 6.357e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 544
L0237 | Coimbatore | Erode | GOBI | ARASUR | Gobichettipalayam | Arasur (TN) | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 55 | 270 | thermal | 270 | 1209 | 0.00013175 | 0.00075208 | 0.0015411 | 11.594 | 66.1827 | 5.2975e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 575
L0255 | Coimbatore | Erode | INGUR | ARASUR | Ingur | Arasur (TN) | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 54 | 270 | thermal | 270 | 1231 | 0.00013175 | 0.00075208 | 0.0015411 | 11.3832 | 64.9793 | 5.2012e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 593 |  | S/C parameters used (D/C not tabulated)
L0257 | Coimbatore | Erode | INGUR | KARAMADAI | Ingur | Karamadai 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 67 | 260 | thermal | 260 | 989 | 0.00014154 | 0.00075473 | 0.001552 | 15.1731 | 80.9069 | 6.4991e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 595 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0305 | Coimbatore | Erode | KARAMADAI | SHENBAGAPUDUR | Karamadai 400/230 | Shenbagapudur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 40 | 270 | thermal | 270 | 1662 | 0.00013175 | 0.00075208 | 0.0015411 | 8.432 | 48.1328 | 3.8527e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 643
L0309 | Coimbatore | Erode | KARUVALUR | SHENBAGAPUDUR | Karuvalur | Shenbagapudur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 37 | 270 | thermal | 270 | 1797 | 0.00013175 | 0.00075208 | 0.0015411 | 7.7996 | 44.5229 | 3.5638e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 647
L0421 | Coimbatore | Erode | PARAMATHY | KURKATHI | Paramathi | Kurkathi | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 54 | 260 | thermal | 260 | 1227 | 0.00014154 | 0.00075473 | 0.001552 | 12.2291 | 65.2086 | 5.2381e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 759 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0038 | Coimbatore | Madurai | MYWADI | MADURAI-PG | Udumalpet / Mywadi (PG) 400/230 | Madurai (PG) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 127 | 1015 | thermal | 1015 | 1897 | 1.862e-05 | 0.0002075 | 0.00555 | 3.7836 | 42.164 | 0.00044053 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 197
L0095 | Coimbatore | Madurai | ANAIKADAVU | THAPAKUNDU | Anaikadavu 400/230 | Thappagundu 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 179 | 1032 | thermal | 1032 | 1453 | 1.8e-05 | 0.0001923 | 0.00602 | 5.1552 | 55.0747 | 0.00067349 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 341
L0096 | Coimbatore | Madurai | ANAIKADAVU | THAPAKUNDU | Anaikadavu 400/230 | Thappagundu 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 179 | 1032 | thermal | 1032 | 1453 | 1.8e-05 | 0.0001923 | 0.00602 | 5.1552 | 55.0747 | 0.00067349 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 342
L0386 | Coimbatore | Madurai | MYWADI | SEMPATTI | Udumalpet / Mywadi (PG) 400/230 | Sempatti | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 80 | 260 | thermal | 260 | 828 | 0.00014154 | 0.00075473 | 0.001552 | 18.1172 | 96.6053 | 7.7601e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 724
L0043 | Coimbatore | Tirunelveli | MYWADI | TIRUNELVELI-PG | Udumalpet / Mywadi (PG) 400/230 | Tirunelveli (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 265 | 981 | stability (30°) | 1032 | 981 | 1.8e-05 | 0.0001923 | 0.00602 | 7.632 | 81.5352 | 0.00099706 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 202
L0044 | Coimbatore | Tirunelveli | MYWADI | TIRUNELVELI-PG | Udumalpet / Mywadi (PG) 400/230 | Tirunelveli (PG) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 265 | 981 | stability (30°) | 1032 | 981 | 1.8e-05 | 0.0001923 | 0.00602 | 7.632 | 81.5352 | 0.00099706 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 203
L0520 | Coimbatore | Trichy | KARUR PS | PUGALUR-PG | Karur ISTS pooling station 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 37 | 2044 | thermal | 2044 | 8542 | 9.177e-06 | 0.0001582 | 0.00733 | 0.54328 | 9.3654 | 0.00016951 | TRUE | Karur Transmission Ltd | in service | high | SR Annual Compendium 2023-24 (SRLDC), Table 34 #14 (LILO), 24-10-2023
L0522 | Coimbatore | Trichy | KARUR PS | PUGALUR-PG | Karur ISTS pooling station 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 37 | 2044 | thermal | 2044 | 8542 | 9.177e-06 | 0.0001582 | 0.00733 | 0.54328 | 9.3654 | 0.00016951 | TRUE | Karur Transmission Ltd | in service | high | SR Annual Compendium 2023-24 (SRLDC), Table 34 #13 (LILO), 24-10-2023
L0058 | Coimbatore | Vellore | PUGALUR HVDC | THIRUVALAM-PG | Pugalur HVDC ±800 kV / VSC terminal | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 390 | 810 | stability (30°) | 2044 | 810 | 9.177e-06 | 0.0001582 | 0.00733 | 5.7264 | 98.7168 | 0.0017867 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 253
L0059 | Coimbatore | Vellore | PUGALUR HVDC | THIRUVALAM-PG | Pugalur HVDC ±800 kV / VSC terminal | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 390 | 810 | stability (30°) | 2044 | 810 | 9.177e-06 | 0.0001582 | 0.00733 | 5.7264 | 98.7168 | 0.0017867 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 254
L0121 | Coimbatore | Vellore | PALAVADI | RASIPALAYAM | Palavadi 400/230 | Rasipalayam 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 194 | 1629 | stability (30°) | 2044 | 1629 | 9.177e-06 | 0.0001582 | 0.00733 | 2.8485 | 49.1053 | 0.00088876 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 369
L0122 | Coimbatore | Vellore | PALAVADI | RASIPALAYAM | Palavadi 400/230 | Rasipalayam 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 194 | 1629 | stability (30°) | 2044 | 1629 | 9.177e-06 | 0.0001582 | 0.00733 | 2.8485 | 49.1053 | 0.00088876 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 370
L0123 | Coimbatore | Vellore | PALAVADI | RASIPALAYAM | Palavadi 400/230 | Rasipalayam 400/230 | 400 | 400 | AC | 3 | D/C | QUAD ACSR MOOSE | 190 | 1663 | stability (30°) | 2044 | 1663 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7898 | 48.0928 | 0.00087044 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 371
L0124 | Coimbatore | Vellore | PALAVADI | RASIPALAYAM | Palavadi 400/230 | Rasipalayam 400/230 | 400 | 400 | AC | 4 | D/C | QUAD ACSR MOOSE | 190 | 1663 | stability (30°) | 2044 | 1663 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7898 | 48.0928 | 0.00087044 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 372
L0161 | Erode | Trichy | PARAMATHY | SPRING-PGLR | Paramathi | Spring Akshaya wind (Pugalur) | 230 | 230 | AC | 1 | S/C | SINGLE ACSR MOOSE | 34 | 260 | thermal | 260 | 1948 | 0.00014154 | 0.00075473 | 0.001552 | 7.6998 | 41.0573 | 3.2981e-05 | TRUE | SPRING-PGLR | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 499
L0187 | Erode | Trichy | ALUNDUR | VALAYAPATTY | Alundur (Trichy) | Valayapatti | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 90 | 260 | thermal | 260 | 736 | 0.00014154 | 0.00075473 | 0.001552 | 20.3818 | 108.681 | 8.7301e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 525
L0422 | Erode | Trichy | PARAMATHY | PUGALUR | Paramathi | Pugalur (TN) 230 | 230 | 230 | AC | 1 | D/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 28 | 260 | thermal | 260 | 2366 | 0.00014154 | 0.00075473 | 0.001552 | 6.341 | 33.8119 | 2.716e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 760 |  | S/C parameters used (D/C not tabulated); mixed sections: weakest (highest-resistance) conductor used for whole line
L0423 | Erode | Trichy | PARAMATHY | PUGALUR | Paramathi | Pugalur (TN) 230 | 230 | 230 | AC | 2 | D/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 28 | 260 | thermal | 260 | 2366 | 0.00014154 | 0.00075473 | 0.001552 | 6.341 | 33.8119 | 2.716e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 761 |  | S/C parameters used (D/C not tabulated); mixed sections: weakest (highest-resistance) conductor used for whole line
L0437 | Erode | Trichy | PUTHANSANTHAI | PUGALUR | Puthanchandai | Pugalur (TN) 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 58 | 260 | thermal | 260 | 1142 | 0.00014154 | 0.00075473 | 0.001552 | 13.1349 | 70.0388 | 5.6261e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 775 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0063 | Erode | Vellore | SALEM-PG | DHARAMAPURI | Salem (PG) 400/230 | Dharmapuri (Salem PS) 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 59 | 2044 | thermal | 2044 | 5357 | 9.177e-06 | 0.0001582 | 0.00733 | 0.86631 | 14.9341 | 0.00027029 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 270
L0064 | Erode | Vellore | SALEM-PG | DHARAMAPURI | Salem (PG) 400/230 | Dharmapuri (Salem PS) 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 59 | 2044 | thermal | 2044 | 5357 | 9.177e-06 | 0.0001582 | 0.00733 | 0.86631 | 14.9341 | 0.00027029 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 271
L0065 | Erode | Vellore | SALEM-PG | HOSUR-PG | Salem (PG) 400/230 | Hosur (PG) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 126 | 1015 | thermal | 1015 | 1912 | 1.862e-05 | 0.0002075 | 0.00555 | 3.7538 | 41.832 | 0.00043706 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 272
L0066 | Erode | Vellore | SALEM-PG | HOSUR-PG | Salem (PG) 400/230 | Hosur (PG) 400/230 | 400 | 400 | AC | 2 | S/C | TWIN ACSR MOOSE | 125 | 1015 | thermal | 1015 | 1928 | 1.862e-05 | 0.0002075 | 0.00555 | 3.724 | 41.5 | 0.00043359 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 273
L0118 | Erode | Vellore | MTPS-3 | PALAVADI | Mettur TPS St-III 400/230 | Palavadi 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 61 | 2044 | thermal | 2044 | 5181 | 9.177e-06 | 0.0001582 | 0.00733 | 0.89568 | 15.4403 | 0.00027946 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 366
L0119 | Erode | Vellore | MTPS-3 | PALAVADI | Mettur TPS St-III 400/230 | Palavadi 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 61 | 2044 | thermal | 2044 | 5181 | 9.177e-06 | 0.0001582 | 0.00733 | 0.89568 | 15.4403 | 0.00027946 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 367
L0249 | Erode | Vellore | HOSUR | METTUR AUTO | Hosur (TN) 230 | Mettur Auto 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 135 | 270 | thermal | 270 | 492 | 0.00013175 | 0.00075208 | 0.0015411 | 28.4581 | 162.4483 | 0.00013003 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 587
L0360 | Erode | Vellore | METTUR AUTO | PALAVADI | Mettur Auto 230 | Palavadi 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 56 | 270 | thermal | 270 | 1187 | 0.00013175 | 0.00075208 | 0.0015411 | 11.8048 | 67.386 | 5.3938e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 698
L0373 | Erode | Vellore | MTPS | SINGARAPET | Mettur TPS St-I/II 230 | Singarapettai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 110 | 260 | thermal | 260 | 602 | 0.00014154 | 0.00075473 | 0.001552 | 24.9111 | 132.8323 | 0.0001067 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 711
L0443 | Erode | Vellore | SALEM | SINGARAPET | Salem (TN) 230 | Singarapettai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 96 | 260 | thermal | 260 | 690 | 0.00014154 | 0.00075473 | 0.001552 | 21.7406 | 115.9264 | 9.3121e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 781
L0069 | Erode | Villupuram | SALEM-PG | NLC STG2 | Salem (PG) 400/230 | NLC TPS-II 400/230 | 400 | 400 | AC | 2 | S/C | TWIN ACSR MOOSE | 175 | 1015 | thermal | 1015 | 1377 | 1.862e-05 | 0.0002075 | 0.00555 | 5.2136 | 58.1 | 0.00060703 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 276
L0070 | Erode | Villupuram | SALEM-PG | NNTPP | Salem (PG) 400/230 | New Neyveli TPS (NNTPP) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 179 | 1015 | thermal | 1015 | 1346 | 1.862e-05 | 0.0002075 | 0.00555 | 5.3328 | 59.428 | 0.00062091 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 277
L0229 | Erode | Villupuram | DEVIYAKURICHI | STCMS | Deviyakurichi | ST-CMS Neyveli | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 90 | 260 | thermal | 260 | 736 | 0.00014154 | 0.00075473 | 0.001552 | 20.3818 | 108.681 | 8.7301e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 567
L0034 | Madurai | Tirunelveli | MADURAI-PG | TUTICORIN-PS | Madurai (PG) 400/230 | Tuticorin PS 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 95 | 2044 | thermal | 2044 | 3327 | 9.177e-06 | 0.0001582 | 0.00733 | 1.3949 | 24.0464 | 0.00043522 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 190
L0035 | Madurai | Tirunelveli | MADURAI-PG | TUTICORIN-PS | Madurai (PG) 400/230 | Tuticorin PS 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 95 | 2044 | thermal | 2044 | 3327 | 9.177e-06 | 0.0001582 | 0.00733 | 1.3949 | 24.0464 | 0.00043522 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 191
L0078 | Madurai | Tirunelveli | TIRUNELVELI-PG | MADURAI-PG | Tirunelveli (PG) 400/230 | Madurai (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 162 | 1032 | thermal | 1032 | 1605 | 1.8e-05 | 0.0001923 | 0.00602 | 4.6656 | 49.8442 | 0.00060952 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 305
L0079 | Madurai | Tirunelveli | TIRUNELVELI-PG | MADURAI-PG | Tirunelveli (PG) 400/230 | Madurai (PG) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 162 | 1032 | thermal | 1032 | 1605 | 1.8e-05 | 0.0001923 | 0.00602 | 4.6656 | 49.8442 | 0.00060952 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 306
L0102 | Madurai | Tirunelveli | KAMUTHI | OTTAPIDARAM | Kamuthi 400/230 | Ottapidaram 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 75 | 2044 | thermal | 2044 | 4214 | 9.177e-06 | 0.0001582 | 0.00733 | 1.1012 | 18.984 | 0.00034359 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 349
L0103 | Madurai | Tirunelveli | KAMUTHI | OTTAPIDARAM | Kamuthi 400/230 | Ottapidaram 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 75 | 2044 | thermal | 2044 | 4214 | 9.177e-06 | 0.0001582 | 0.00733 | 1.1012 | 18.984 | 0.00034359 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 350
L0106 | Madurai | Tirunelveli | KARAIKUDI-PG | KAYATHAR | Karaikudi (PG) 400/230 | Kayathar 400/230/110 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 195 | 1621 | stability (30°) | 2044 | 1621 | 9.177e-06 | 0.0001582 | 0.00733 | 2.8632 | 49.3584 | 0.00089334 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 353
L0107 | Madurai | Tirunelveli | KARAIKUDI-PG | KAYATHAR | Karaikudi (PG) 400/230 | Kayathar 400/230/110 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 195 | 1621 | stability (30°) | 2044 | 1621 | 9.177e-06 | 0.0001582 | 0.00733 | 2.8632 | 49.3584 | 0.00089334 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 354
L0188 | Madurai | Tirunelveli | AMUDHAPURAM | CHECKANURANI | Amudhapuram | Checkanurani | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 112 | 270 | thermal | 270 | 594 | 0.00013175 | 0.00075208 | 0.0015411 | 23.6097 | 134.772 | 0.00010788 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 526
L0195 | Madurai | Tirunelveli | ANUPANKULAM | PASUMALAI | Anuppankulam | Pasumalai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 75 | 260 | thermal | 260 | 883 | 0.00014154 | 0.00075473 | 0.001552 | 16.9848 | 90.5675 | 7.2751e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 533
L0215 | Madurai | Tirunelveli | CHECKANURANI | IND BHARATH 2 | Checkanurani | Ind-Barath 2 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 134 | 270 | thermal | 270 | 496 | 0.00013175 | 0.00075208 | 0.0015411 | 28.2473 | 161.245 | 0.00012907 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 553
L0216 | Madurai | Tirunelveli | CHECKANURANI | KAYATHAR 230/110 | Checkanurani | Kayathar (old) 230/110 | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 148 | 270 | thermal | 270 | 449 | 0.00013175 | 0.00075208 | 0.0015411 | 31.1985 | 178.0915 | 0.00014255 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 554 |  | S/C parameters used (D/C not tabulated)
L0218 | Madurai | Tirunelveli | CHECKANURANI | NALLAMANAICKENPATTI | Checkanurani | Nallamanaickenpatti | 230 | 230 | AC | 2 | S/C | SINGLE ACSR ZEBRA | 85 | 270 | thermal | 270 | 782 | 0.00013175 | 0.00075208 | 0.0015411 | 17.9181 | 102.2823 | 8.1871e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 556
L0221 | Madurai | Tirunelveli | CHECKANURANI | SAVASPURAM | Checkanurani | Savaspuram | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 68 | 270 | thermal | 270 | 978 | 0.00013175 | 0.00075208 | 0.0015411 | 14.3345 | 81.8258 | 6.5497e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 559
L0223 | Madurai | Tirunelveli | CHECKANURANI | TTPS | Checkanurani | Tuticorin TPS 230 | 230 | 230 | AC | 2 | D/C | SINGLE ACSR KUNDAH | 148 | 260 | thermal | 260 | 448 | 0.00014154 | 0.00075473 | 0.001552 | 33.5167 | 178.7198 | 0.00014356 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 561 |  | S/C parameters used (D/C not tabulated)
L0284 | Madurai | Tirunelveli | KAMUTHI | TIRUCHULI | Kamuthi 400/230 | Tiruchuli | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 45 | 270 | thermal | 270 | 1477 | 0.00013175 | 0.00075208 | 0.0015411 | 9.486 | 54.1494 | 4.3343e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 622 |  | S/C parameters used (D/C not tabulated)
L0285 | Madurai | Tirunelveli | KAMUTHI | TIRUCHULI | Kamuthi 400/230 | Tiruchuli | 230 | 230 | AC | 2 | D/C | SINGLE ACSR ZEBRA | 45 | 270 | thermal | 270 | 1477 | 0.00013175 | 0.00075208 | 0.0015411 | 9.486 | 54.1494 | 4.3343e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 623 |  | S/C parameters used (D/C not tabulated)
L0286 | Madurai | Tirunelveli | KAMUTHI | TIRUCHULI | Kamuthi 400/230 | Tiruchuli | 230 | 230 | AC | 3 | D/C | SINGLE ACSR ZEBRA | 45 | 270 | thermal | 270 | 1477 | 0.00013175 | 0.00075208 | 0.0015411 | 9.486 | 54.1494 | 4.3343e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 624 |  | S/C parameters used (D/C not tabulated)
L0312 | Madurai | Tirunelveli | KAVANUR | MILAVITTAN | Kavanur | Milavittan | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 106 | 260 | thermal | 260 | 625 | 0.00014154 | 0.00075473 | 0.001552 | 24.0052 | 128.002 | 0.00010282 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 650 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0316 | Madurai | Tirunelveli | KAYATHAR 230/110 | KINNIMANGALAM | Kayathar (old) 230/110 | Kinnimangalam | 230 | 230 | AC | 2 | D/C | SINGLE ACSR KUNDAH | 148 | 260 | thermal | 260 | 448 | 0.00014154 | 0.00075473 | 0.001552 | 33.5167 | 178.7198 | 0.00014356 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 654 |  | S/C parameters used (D/C not tabulated)
L0425 | Madurai | Tirunelveli | PASUMALAI | KAYATHAR | Pasumalai | Kayathar 400/230/110 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 126 | 260 | thermal | 260 | 526 | 0.00014154 | 0.00075473 | 0.001552 | 28.5345 | 152.1534 | 0.00012222 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 763
L0428 | Madurai | Tirunelveli | PASUMALAI | TTPS | Pasumalai | Tuticorin TPS 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 138 | 260 | thermal | 260 | 480 | 0.00014154 | 0.00075473 | 0.001552 | 31.2521 | 166.6441 | 0.00013386 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 766
L0495 | Madurai | Tirunelveli | TTPS | KINNIMANGALAM | Tuticorin TPS 230 | Kinnimangalam | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 142 | 260 | thermal | 260 | 467 | 0.00014154 | 0.00075473 | 0.001552 | 32.1579 | 171.4744 | 0.00013774 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 833
L0032 | Madurai | Trichy | MADURAI-PG | PUGALUR-PG | Madurai (PG) 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 124 | 1032 | thermal | 1032 | 2097 | 1.8e-05 | 0.0001923 | 0.00602 | 3.5712 | 38.1523 | 0.00046655 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 188
L0033 | Madurai | Trichy | MADURAI-PG | PUGALUR-PG | Madurai (PG) 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 124 | 1032 | thermal | 1032 | 2097 | 1.8e-05 | 0.0001923 | 0.00602 | 3.5712 | 38.1523 | 0.00046655 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 189
L0083 | Madurai | Trichy | TRICHY-PG | KARAIKUDI-PG | Trichy (PG) 400/230 | Karaikudi (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 98 | 1032 | thermal | 1032 | 2653 | 1.8e-05 | 0.0001923 | 0.00602 | 2.8224 | 30.1526 | 0.00036872 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 316
L0084 | Madurai | Trichy | TRICHY-PG | MADURAI-PG | Trichy (PG) 400/230 | Madurai (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 130 | 1032 | thermal | 1032 | 2000 | 1.8e-05 | 0.0001923 | 0.00602 | 3.744 | 39.9984 | 0.00048913 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 317
L0108 | Madurai | Trichy | KARAIKUDI-PG | PUGALUR-PG | Karaikudi (PG) 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 160 | 1975 | stability (30°) | 2044 | 1975 | 9.177e-06 | 0.0001582 | 0.00733 | 2.3493 | 40.4992 | 0.000733 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 355
L0109 | Madurai | Trichy | KARAIKUDI-PG | PUGALUR-PG | Karaikudi (PG) 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 160 | 1975 | stability (30°) | 2044 | 1975 | 9.177e-06 | 0.0001582 | 0.00733 | 2.3493 | 40.4992 | 0.000733 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 356
L0110 | Madurai | Trichy | KARAIKUDI-PG | VELLALVDUTHI | Karaikudi (PG) 400/230 | Vellalaviduthi 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 145 | 2044 | thermal | 2044 | 2180 | 9.177e-06 | 0.0001582 | 0.00733 | 2.1291 | 36.7024 | 0.00066428 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 357
L0169 | Madurai | Trichy | ALAGAR KOVIL | MANDIPATTI | Alagarkovil | Mandipatti | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 105 | 260 | thermal | 260 | 631 | 0.00014154 | 0.00075473 | 0.001552 | 23.7788 | 126.7945 | 0.00010185 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 507 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0292 | Madurai | Trichy | KARAIKUDI 230/110 | KARAMBAYAM | Karaikudi (TN) 230/110 | Karambayam | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 88 | 260 | thermal | 260 | 753 | 0.00014154 | 0.00075473 | 0.001552 | 19.9289 | 106.2658 | 8.5361e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 630 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0293 | Madurai | Trichy | KARAIKUDI 230/110 | KARAMBAYAM | Karaikudi (TN) 230/110 | Karambayam | 230 | 230 | AC | 2 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 88 | 260 | thermal | 260 | 753 | 0.00014154 | 0.00075473 | 0.001552 | 19.9289 | 106.2658 | 8.5361e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 631 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0301 | Madurai | Trichy | KARAIKUDI-PG | PUDUKOTAI | Karaikudi (PG) 400/230 | Pudukkottai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 49 | 270 | thermal | 270 | 1357 | 0.00013175 | 0.00075208 | 0.0015411 | 10.3292 | 58.9627 | 4.7196e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 639
L0435 | Madurai | Trichy | PUGALUR | RENGANATHAPURAM | Pugalur (TN) 230 | Renganathapuram | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 60 | 260 | thermal | 260 | 1104 | 0.00014154 | 0.00075473 | 0.001552 | 13.5879 | 72.454 | 5.8201e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 773 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0005 | Tirunelveli | Vellore | DHARAMAPURI | TUTICORIN-PS | Dharmapuri (Salem PS) 765/400 | Tuticorin PS 765/400 | 400 | 765 | AC | 1 | D/C | HEXA ACSR ZEBRA | 369 | 850 | stability (30°) | 2739 | 850 | 7.6664e-06 | 0.00015947 | 0.0072724 | 4.5263 | 94.1533 | 0.0016772 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 27 | Built for 765 kV, operated at 400 kV (2023)
L0006 | Tirunelveli | Vellore | DHARAMAPURI | TUTICORIN-PS | Dharmapuri (Salem PS) 765/400 | Tuticorin PS 765/400 | 400 | 765 | AC | 2 | D/C | HEXA ACSR ZEBRA | 369 | 850 | stability (30°) | 2739 | 850 | 7.6664e-06 | 0.00015947 | 0.0072724 | 4.5263 | 94.1533 | 0.0016772 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 28 | Built for 765 kV, operated at 400 kV (2023)
L0052 | Trichy | Villupuram | NLC STG2 | PUGALUR-PG | NLC TPS-II 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 198 | 1032 | thermal | 1032 | 1313 | 1.8e-05 | 0.0001923 | 0.00602 | 5.7024 | 60.9206 | 0.00074498 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 230
L0060 | Trichy | Villupuram | PUGALUR-PG | NLC STG2 EXP | Pugalur (PG) 400/230 | NLC TPS-II Expansion 400 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 200 | 1032 | thermal | 1032 | 1300 | 1.8e-05 | 0.0001923 | 0.00602 | 5.76 | 61.536 | 0.0007525 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 255
L0061 | Trichy | Villupuram | PUGALUR-PG | NNTPP | Pugalur (PG) 400/230 | New Neyveli TPS (NNTPP) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 258 | 1008 | stability (30°) | 1032 | 1008 | 1.8e-05 | 0.0001923 | 0.00602 | 7.4304 | 79.3814 | 0.00097073 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 256
L0085 | Trichy | Villupuram | TRICHY-PG | NAGAPATINAM-PS | Trichy (PG) 400/230 | Nagapattinam PS 765/400 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 159 | 1032 | thermal | 1032 | 1635 | 1.8e-05 | 0.0001923 | 0.00602 | 4.5792 | 48.9211 | 0.00059824 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 318
L0086 | Trichy | Villupuram | TRICHY-PG | NAGAPATINAM-PS | Trichy (PG) 400/230 | Nagapattinam PS 765/400 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 159 | 1032 | thermal | 1032 | 1635 | 1.8e-05 | 0.0001923 | 0.00602 | 4.5792 | 48.9211 | 0.00059824 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 319
L0125 | Trichy | Villupuram | PUGALUR-PG | ARIYALUR | Pugalur (PG) 400/230 | Ariyalur 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 184 | 1718 | stability (30°) | 2044 | 1718 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7017 | 46.5741 | 0.00084295 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 373
L0518 | Trichy | Villupuram | PUGALUR-PG | ARIYALUR | Pugalur (PG) 400/230 | Ariyalur 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 185 | 1708 | stability (30°) | 2044 | 1708 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7164 | 46.8272 | 0.00084753 | TRUE | TANTRANSCO | in service | high | SR Annual Compendium 2023-24 (SRLDC), Table 34 #19 (LILO), 10-02-2024
L0231 | Trichy | Villupuram | EACHANGADU | NLC TNEB | Eachangadu | Neyveli (TNEB) 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 45 | 260 | thermal | 260 | 1472 | 0.00014154 | 0.00075473 | 0.001552 | 10.1909 | 54.3405 | 4.3651e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 569
L0266 | Trichy | Villupuram | KADALANGUDY | NLC STG2 | Kadalangudy | NLC TPS-II 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 92 | 260 | thermal | 260 | 720 | 0.00014154 | 0.00075473 | 0.001552 | 20.8347 | 111.0961 | 8.9241e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 604
L0267 | Trichy | Villupuram | KADALANGUDY | NLC TNEB | Kadalangudy | Neyveli (TNEB) 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 77 | 270 | thermal | 270 | 863 | 0.00013175 | 0.00075208 | 0.0015411 | 16.2317 | 92.6557 | 7.4165e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 605
L0465 | Trichy | Villupuram | STCMS | PERMBALUR | ST-CMS Neyveli | Perambalur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 64 | 260 | thermal | 260 | 1035 | 0.00014154 | 0.00075473 | 0.001552 | 14.4937 | 77.2842 | 6.2081e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 803
L0529 | Vellore | Villupuram | THIRUVALAM-PG | ARIYALUR | Thiruvalam (PG) 765/400 | Ariyalur 765/400 | 765 | 765 | AC | 2 | D/C | HEXA ACSR ZEBRA | 173.56 | 5238 | thermal | 5238 | 6607 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.58205 | 12.1075 | 0.0028854 | TRUE | TANTRANSCO | in service | high | SR Annual Compendium 2023-24 (SRLDC), Table 33 #22, 27-12-2023 | Same circuit also listed as #14 with 120 km on 20-10-2023 (likely partial charging); Thiruvalam end assumed to be the 765 kV (PG) bus
L0545 | Vellore | Villupuram | THIRUVALAM-PG | ARIYALUR | Thiruvalam (PG) 765/400 | Ariyalur 765/400 | 765 | 765 | AC | 1 | D/C | HEXA ACSR ZEBRA | 173.569 | 5238 | thermal | 5238 | 6607 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.58208 | 12.1082 | 0.0028856 | TRUE | TANTRANSCO | in service | high | SR Annual Compendium 2025-26 (SRLDC), Table 57, charged 03-12-2025 | Thiruvalam end assumed to be the existing 765 kV (PG) bus; 240 MVAr line reactor at Ariyalur
L0003 | Vellore | Villupuram | DHARAMAPURI | NAGAPATINAM-PS | Dharmapuri (Salem PS) 765/400 | Nagapattinam PS 765/400 | 400 | 765 | AC | 1 | D/C | HEXA ACSR ZEBRA | 204 | 1537 | stability (30°) | 2739 | 1537 | 7.6664e-06 | 0.00015947 | 0.0072724 | 2.5023 | 52.0523 | 0.00092723 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 25 | Built for 765 kV, operated at 400 kV (2023)
L0004 | Vellore | Villupuram | DHARAMAPURI | NAGAPATINAM-PS | Dharmapuri (Salem PS) 765/400 | Nagapattinam PS 765/400 | 400 | 765 | AC | 2 | D/C | HEXA ACSR ZEBRA | 204 | 1537 | stability (30°) | 2739 | 1537 | 7.6664e-06 | 0.00015947 | 0.0072724 | 2.5023 | 52.0523 | 0.00092723 | TRUE | PGCIL | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 26 | Built for 765 kV, operated at 400 kV (2023)
L0199 | Vellore | Villupuram | ARANI | SINGARAPET | Arani | Singarapettai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 98 | 260 | thermal | 260 | 676 | 0.00014154 | 0.00075473 | 0.001552 | 22.1935 | 118.3415 | 9.5062e-05 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 537
L0454 | Vellore | Villupuram | SINGARAPET | THIRUVANAMALAI | Singarapettai | Tiruvannamalai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 111 | 260 | thermal | 260 | 597 | 0.00014154 | 0.00075473 | 0.001552 | 25.1376 | 134.0399 | 0.00010767 | TRUE | TANTRANSCO | in service | high | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 792

## network
name | _multi_invest | pypsa_version | srid
Tamil Nadu 9 balancing areas – inter-area transmission, end FY2025-26 | 0 | 1.4.0 | 4326

## crs
Key | Value
_crs | GEOGCRS["WGS 84",ENSEMBLE["World Geodetic System 1984 ensemble",MEMBER["World Geodetic System 1984 (Transit)"],MEMBER["World Geodetic System 1984 (G730)"],MEMBER["World Geodetic System 1984 (G873)"],MEMBER["World Geodetic System 1984 (G1150)"],MEMBER["World Geodetic System 1984 (G1674)"],MEMBER["World Geodetic System 1984 (G1762)"],MEMBER["World Geodetic System 1984 (G2139)"],MEMBER["World Geodetic System 1984 (G2296)"],ELLIPSOID["WGS 84",6378137,298.257223563,LENGTHUNIT["metre",1]],ENSEMBLEACCURACY[2.0]],PRIMEM["Greenwich",0,ANGLEUNIT["degree",0.0174532925199433]],CS[ellipsoidal,2],AXIS["geodetic latitude (Lat)",north,ORDER[1],ANGLEUNIT["degree",0.0174532925199433]],AXIS["geodetic longitude (Lon)",east,ORDER[2],ANGLEUNIT["degree",0.0174532925199433]],USAGE[SCOPE["Horizontal component of 3D system."],AREA["World."],BBOX[-90,-180,90,180]],ID["EPSG",4326]]

## meta
Key | Value

## snapshots
| snapshot | objective | stores | generators
0 | now | 1 | 1 | 1