## README
Tamil Nadu – 9 balancing areas with interconnectors to neighbouring states (end of FY2025-26)
PyPSA network. Load with: n = pypsa.Network(); n.import_from_excel('TN_9BA_with_interconnectors_pypsa_FY2025-26.xlsx') (tested with PyPSA 1.4). This README and the 'circuits' sheet are ignored on import.
What is in it
buses (14): the 9 TN balancing areas + Andhra Pradesh, Karnataka, Kerala, Puducherry and the Western Region (far end of the Raigarh–Pugalur HVDC). x/y = map anchor (lon/lat); v_nom = 400 kV reference; column 'kind' tells TN areas from neighbours. within_area_mw / within_area_circuits = sum of ratings of circuits inside each TN area (informational).
lines (active): 18 AC equivalents between the TN areas (120,072 MW), DC power flow. One branch per pair: s_nom = sum of circuit ratings (MW); s_max_pu = 0.7, so the usable limit is 70% of s_nom (change with n.lines['s_max_pu'] = …); x, r = parallel combination of circuit impedances in ohm at 400 kV; b = summed susceptance (S). Extra columns: kind, s_nom_n1 (sum minus largest circuit), largest_circuit_mw, n_circuits, circuits_by_kv, mw_by_kv, line_ids.
links (active): 10 interstate AC ties ('… (AC tie)', 43,520 MW) and 2 HVDC links (HVDC Raigarh–Pugalur Coimbatore–Western Region 6,000 MW; HVDC Pugalur–Thrissur Coimbatore–Kerala 2,000 MW), each as TWO one-way links: '… →' = out of Tamil Nadu (bus0 = TN area), '… ←' = into Tamil Nadu (bus0 = neighbour). p_nom = sum of circuit ratings (or converter rating), p_min_pu = 0, marginal_cost = 0.01 per MWh – a tiny wheeling charge so the optimiser does not circulate lossless flow out through one tie and back through another (a single bidirectional link cannot do this, because PyPSA charges marginal_cost on signed flow). Net flow on a tie = p0('→') − p0('←'). Columns pair, direction, p_nom_n1, largest_circuit_mw, n_circuits, circuits_by_kv, x_equivalent_ohm (to rebuild a line if wanted) and line_ids describe each tie.
links (inactive): '… (transport)' duplicates of the TN inter-area lines. Pure transport model: n.lines['active'] = False; n.links.loc[n.links.index.str.endswith('(transport)'), 'active'] = True.
circuits: every circuit crossing an area or state boundary, with endpoints, conductor, length, per-unit and ohmic parameters, rating, limit type and source.
No generators, loads, storage or snapshots – add your own.
How the numbers were made
Circuit rating = min(thermal, 30° angular-stability limit). Thermal: ACSR Moose 1,068 MW per 400 kV twin circuit at 40 °C ambient / 75 °C conductor (Pentayya et al., 'Line Loadability in Indian Perspective', NPSC 2012), scaled by sqrt(R_Moose/R) per conductor, 0.95 power factor. Stability: P = 100·sin30°/(x_pu·L). R, X, B from the line-parameter table of the SRLDC Compendium of SR Transmission Elements 2023 (pu/km on 100 MVA, re-based to the operating voltage). HVDC: converter ratings from the compendium (Raigarh–Pugalur 4 × 1,500 MW LCC; Pugalur–Thrissur 2 × 1,000 MW VSC).
Per-unit impedances on a common 100 MVA base are voltage-independent, so 765 kV and 230/220/110 kV circuits are combined with 400 kV ones by converting pu to ohm at 400 kV (Z_base = 1,600 ohm). Transformers between voltage levels are not modelled.
Network: SRLDC Compendium of SR Transmission Elements 2023 (as of 31-05-2023) + new lines and LILO re-arrangements in the SR Annual Compendiums 2023-24, 2024-25 and 2025-26. Substations placed with OpenStreetMap and assigned to areas by polygon. Only lines touching Tamil Nadu or Puducherry are included.
Caveats – read before using
1. Neighbours are single nodes and are NOT connected to each other. In reality Andhra Pradesh, Karnataka and Kerala are tied directly (and to the rest of India), so a DC power flow on this file will push all AP/Karnataka→Kerala transit through Tamil Nadu. Either fix the neighbours' exchanges (e.g. generators/loads with given p_set at the neighbour buses, or p_max_pu = p_min_pu on the ties), or add external equivalent lines between neighbours (e.g. Karnataka–Kerala, AP–Karnataka) before using flows.
2. s_nom is a sum of circuit ratings, not a transfer capability. On the S1→(S2+S3) corridor (AP/Telangana/Karnataka → TN/Puducherry/Kerala) the sum of ratings is roughly 3× Grid-India's TTC (11,300 MW in FY2025-26), mainly because the 400/230 kV transformers at Kalivandapattu and Pugalur bind. Kerala import TTC is 4,575 MW; Southern Region import TTC is 22,300 MW. Calibrate s_max_pu (e.g. 0.3–0.7) or derive NTCs.
3. HVDC: '→' = out of Tamil Nadu, '←' = into Tamil Nadu. Raigarh–Pugalur export (SR→WR) is restricted to about 3,000 MW in operation (SR Annual Compendium 2025-26), import up to 6,000 MW: this is applied – 'HVDC Raigarh–Pugalur →' has p_max_pu = 0.5 (3,000 MW); '←' (import) keeps 1.0 (6,000 MW). Link efficiency is 1 (losses not modelled).
4. Equivalent x per pair ignores impedance inside the areas and inside neighbouring states, so PTDFs are approximate. For accurate flows use the nodal network (tn_lines.csv) and aggregate afterwards.
5. 230 kV TANTRANSCO lines are as of May 2023; 230 kV additions since then are not itemised in any SRLDC source. 400 kV and above are complete to March 2026.
6. NLC TPS-II–Karaikal 230 kV has no length in the source: its impedance uses 1.25 × straight-line distance (column length_estimated). Excluded: circuits without parameters (Kadaperi–Alandur CMRL 230 kV cable; Kuzhithurai–Parassala 110 kV) – see 'circuits', rated = FALSE; Sholinganallur–Tharamani 400 kV (isolator open March 2026).
7. Why the interstate ties are links: with each neighbour as a single node, a DC power flow splits a neighbour's injection over all its ties by impedance, so a small tie (e.g. the 249 MW Sullurpeta–Gummidipoondi 220 kV, Chennai North–AP) hits its limit first and caps the whole import. As links each tie is limited only by its own rating. Small ties in parallel with large ones inside TN can still bind artificially in the DC flow.
8. Transmission reliability margin per Grid-India: largest unit in the importing area or 2% of peak demand – subtract it if you derive NTCs.

## links
name | bus0 | bus1 | carrier | active | p_nom | p_min_pu | p_max_pu | marginal_cost | length | kind | direction | pair | p_nom_n1 | largest_circuit_mw | n_circuits | circuits_by_kv | x_equivalent_ohm | line_ids
HVDC Raigarh–Pugalur → | Coimbatore | Western Region | DC | TRUE | 6000 | 0 | 0.5 | 0.01 | 1765 | HVDC | out of TN | HVDC Raigarh–Pugalur | 0 | 6000 | 1 | ±800 kV HVDC |  | L0548
HVDC Raigarh–Pugalur ← | Western Region | Coimbatore | DC | TRUE | 6000 | 0 | 1 | 0.01 | 1765 | HVDC | into TN | HVDC Raigarh–Pugalur | 0 | 6000 | 1 | ±800 kV HVDC |  | L0548
HVDC Pugalur–Thrissur → | Coimbatore | Kerala | DC | TRUE | 2000 | 0 | 1 | 0.01 | 165 | HVDC | out of TN | HVDC Pugalur–Thrissur | 0 | 2000 | 1 | ±320 kV HVDC |  | L0549
HVDC Pugalur–Thrissur ← | Kerala | Coimbatore | DC | TRUE | 2000 | 0 | 1 | 0.01 | 165 | HVDC | into TN | HVDC Pugalur–Thrissur | 0 | 2000 | 1 | ±320 kV HVDC |  | L0549
Vellore–Andhra Pradesh (AC tie) → | Vellore | Andhra Pradesh | AC | TRUE | 17353 | 0 | 1 | 0.01 | 129.6 | interstate AC tie | out of TN | Vellore–Andhra Pradesh (AC tie) | 12672 | 4681 | 7 | 765 kV ×2; 400 kV ×4; 220 kV ×1 | 1.771 | L0001 L0002 L0021 L0022 L0047 L0048 L0513
Vellore–Andhra Pradesh (AC tie) ← | Andhra Pradesh | Vellore | AC | TRUE | 17353 | 0 | 1 | 0.01 | 129.6 | interstate AC tie | into TN | Vellore–Andhra Pradesh (AC tie) | 12672 | 4681 | 7 | 765 kV ×2; 400 kV ×4; 220 kV ×1 | 1.771 | L0001 L0002 L0021 L0022 L0047 L0048 L0513
Vellore–Karnataka (AC tie) → | Vellore | Karnataka | AC | TRUE | 10115 | 0 | 1 | 0.01 | 120.9 | interstate AC tie | out of TN | Vellore–Karnataka (AC tie) | 8071 | 2044 | 8 | 400 kV ×7; 220 kV ×1 | 4.0044 | L0007 L0008 L0028 L0029 L0071 L0072 L0073 L0515
Vellore–Karnataka (AC tie) ← | Karnataka | Vellore | AC | TRUE | 10115 | 0 | 1 | 0.01 | 120.9 | interstate AC tie | into TN | Vellore–Karnataka (AC tie) | 8071 | 2044 | 8 | 400 kV ×7; 220 kV ×1 | 4.0044 | L0007 L0008 L0028 L0029 L0071 L0072 L0073 L0515
Tirunelveli–Kerala (AC tie) → | Tirunelveli | Kerala | AC | TRUE | 6558 | 0 | 1 | 0.01 | 143.4 | interstate AC tie | out of TN | Tirunelveli–Kerala (AC tie) | 4879 | 1679 | 7 | 400 kV ×4; 220 kV ×2; 110 kV ×1 | 9.3846 | L0080 L0081 L0135 L0136 L0516 L0523 L0524
Tirunelveli–Kerala (AC tie) ← | Kerala | Tirunelveli | AC | TRUE | 6558 | 0 | 1 | 0.01 | 143.4 | interstate AC tie | into TN | Tirunelveli–Kerala (AC tie) | 4879 | 1679 | 7 | 400 kV ×4; 220 kV ×2; 110 kV ×1 | 9.3846 | L0080 L0081 L0135 L0136 L0516 L0523 L0524
Chennai South–Andhra Pradesh (AC tie) → | Chennai South | Andhra Pradesh | AC | TRUE | 3079 | 0 | 1 | 0.01 | 157.7 | interstate AC tie | out of TN | Chennai South–Andhra Pradesh (AC tie) | 2047 | 1032 | 3 | 400 kV ×3 | 15.129 | L0020 L0045 L0046
Chennai South–Andhra Pradesh (AC tie) ← | Andhra Pradesh | Chennai South | AC | TRUE | 3079 | 0 | 1 | 0.01 | 157.7 | interstate AC tie | into TN | Chennai South–Andhra Pradesh (AC tie) | 2047 | 1032 | 3 | 400 kV ×3 | 15.129 | L0020 L0045 L0046
Coimbatore–Kerala (AC tie) → | Coimbatore | Kerala | AC | TRUE | 2324 | 0 | 1 | 0.01 | 86.3 | interstate AC tie | out of TN | Coimbatore–Kerala (AC tie) | 1292 | 1032 | 3 | 400 kV ×2; 230 kV ×1 | 12.5029 | L0039 L0040 L0139
Coimbatore–Kerala (AC tie) ← | Kerala | Coimbatore | AC | TRUE | 2324 | 0 | 1 | 0.01 | 86.3 | interstate AC tie | into TN | Coimbatore–Kerala (AC tie) | 1292 | 1032 | 3 | 400 kV ×2; 230 kV ×1 | 12.5029 | L0039 L0040 L0139
Villupuram–Puducherry (AC tie) → | Villupuram | Puducherry | AC | TRUE | 1535 | 0 | 1 | 0.01 | 76.9 | interstate AC tie | out of TN | Villupuram–Puducherry (AC tie) | 520 | 1015 | 3 | 400 kV ×1; 230 kV ×2 | 14.9707 | L0055 L0155 L0156
Villupuram–Puducherry (AC tie) ← | Puducherry | Villupuram | AC | TRUE | 1535 | 0 | 1 | 0.01 | 76.9 | interstate AC tie | into TN | Villupuram–Puducherry (AC tie) | 520 | 1015 | 3 | 400 kV ×1; 230 kV ×2 | 14.9707 | L0055 L0155 L0156
Chennai South–Karnataka (AC tie) → | Chennai South | Karnataka | AC | TRUE | 1032 | 0 | 1 | 0.01 | 238 | interstate AC tie | out of TN | Chennai South–Karnataka (AC tie) | 0 | 1032 | 1 | 400 kV ×1 | 73.2278 | L0030
Chennai South–Karnataka (AC tie) ← | Karnataka | Chennai South | AC | TRUE | 1032 | 0 | 1 | 0.01 | 238 | interstate AC tie | into TN | Chennai South–Karnataka (AC tie) | 0 | 1032 | 1 | 400 kV ×1 | 73.2278 | L0030
Chennai South–Puducherry (AC tie) → | Chennai South | Puducherry | AC | TRUE | 1015 | 0 | 1 | 0.01 | 129 | interstate AC tie | out of TN | Chennai South–Puducherry (AC tie) | 0 | 1015 | 1 | 400 kV ×1 | 42.828 | L0062
Chennai South–Puducherry (AC tie) ← | Puducherry | Chennai South | AC | TRUE | 1015 | 0 | 1 | 0.01 | 129 | interstate AC tie | into TN | Chennai South–Puducherry (AC tie) | 0 | 1015 | 1 | 400 kV ×1 | 42.828 | L0062
Madurai–Kerala (AC tie) → | Madurai | Kerala | AC | TRUE | 260 | 0 | 1 | 0.01 | 133 | interstate AC tie | out of TN | Madurai–Kerala (AC tie) | 0 | 260 | 1 | 230 kV ×1 | 160.6063 | L0510
Madurai–Kerala (AC tie) ← | Kerala | Madurai | AC | TRUE | 260 | 0 | 1 | 0.01 | 133 | interstate AC tie | into TN | Madurai–Kerala (AC tie) | 0 | 260 | 1 | 230 kV ×1 | 160.6063 | L0510
Chennai North–Andhra Pradesh (AC tie) → | Chennai North | Andhra Pradesh | AC | TRUE | 249 | 0 | 1 | 0.01 | 49 | interstate AC tie | out of TN | Chennai North–Andhra Pradesh (AC tie) | 0 | 249 | 1 | 220 kV ×1 | 64.6722 | L0514
Chennai North–Andhra Pradesh (AC tie) ← | Andhra Pradesh | Chennai North | AC | TRUE | 249 | 0 | 1 | 0.01 | 49 | interstate AC tie | into TN | Chennai North–Andhra Pradesh (AC tie) | 0 | 249 | 1 | 220 kV ×1 | 64.6722 | L0514
Madurai–Tirunelveli (transport) | Madurai | Tirunelveli | AC | FALSE | 17462 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Madurai–Tirunelveli | 15418 | 2044 | 23 | 400 kV ×8; 230 kV ×15 | 2.4215 | L0034 L0035 L0078 L0079 L0102 L0103 L0106 L0107 L0188 L0195 L0215 L0216 L0218 L0221 L0223 L0284 L0285 L0286 L0312 L0316 L0425 L0428 L0495
Vellore–Villupuram (transport) | Vellore | Villupuram | AC | FALSE | 14070 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Vellore–Villupuram | 8832 | 5238 | 6 | 765 kV ×2; 400 kV ×2; 230 kV ×2 | 4.5613 | L0003 L0004 L0199 L0454 L0529 L0545
Madurai–Trichy (transport) | Madurai | Trichy | AC | FALSE | 11432 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Madurai–Trichy | 9388 | 2044 | 12 | 400 kV ×7; 230 kV ×5 | 4.0957 | L0032 L0033 L0083 L0084 L0108 L0109 L0110 L0169 L0292 L0293 L0301 L0435
Erode–Vellore (transport) | Erode | Vellore | AC | FALSE | 11266 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Erode–Vellore | 9222 | 2044 | 10 | 400 kV ×6; 230 kV ×4 | 2.8726 | L0063 L0064 L0065 L0066 L0118 L0119 L0249 L0360 L0373 L0443
Trichy–Villupuram (transport) | Trichy | Villupuram | AC | FALSE | 9612 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Trichy–Villupuram | 7894 | 1718 | 11 | 400 kV ×7; 230 kV ×4 | 5.5651 | L0052 L0060 L0061 L0085 L0086 L0125 L0231 L0266 L0267 L0465 L0518
Chennai North–Villupuram (transport) | Chennai North | Villupuram | AC | FALSE | 8416 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Chennai North–Villupuram | 4208 | 4208 | 2 | 765 kV ×2 | 9.5062 | L0525 L0527
Chennai North–Chennai South (transport) | Chennai North | Chennai South | AC | FALSE | 8282 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Chennai North–Chennai South | 7250 | 1032 | 15 | 400 kV ×6; 230 kV ×9 | 1.9446 | L0025 L0026 L0093 L0094 L0129 L0273 L0275 L0280 L0338 L0341 L0388 L0462 L0463 L0470 L0544
Coimbatore–Vellore (transport) | Coimbatore | Vellore | AC | FALSE | 8204 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Coimbatore–Vellore | 6541 | 1663 | 6 | 400 kV ×6 | 9.749 | L0058 L0059 L0121 L0122 L0123 L0124
Coimbatore–Erode (transport) | Coimbatore | Erode | AC | FALSE | 6224 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Coimbatore–Erode | 5192 | 1032 | 12 | 400 kV ×4; 230 kV ×8 | 4.6355 | L0067 L0068 L0116 L0117 L0202 L0206 L0237 L0255 L0257 L0305 L0309 L0421
Chennai South–Villupuram (transport) | Chennai South | Villupuram | AC | FALSE | 5247 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Chennai South–Villupuram | 3539 | 1708 | 9 | 400 kV ×2; 230 kV ×7 | 9.1087 | L0099 L0147 L0148 L0168 L0197 L0198 L0505 L0506 L0517
Coimbatore–Trichy (transport) | Coimbatore | Trichy | AC | FALSE | 4088 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Coimbatore–Trichy | 2044 | 2044 | 2 | 400 kV ×2 | 4.6827 | L0520 L0522
Coimbatore–Madurai (transport) | Coimbatore | Madurai | AC | FALSE | 3339 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Coimbatore–Madurai | 2307 | 1032 | 4 | 400 kV ×3; 230 kV ×1 | 14.2239 | L0038 L0095 L0096 L0386
Chennai North–Vellore (transport) | Chennai North | Vellore | AC | FALSE | 2594 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Chennai North–Vellore | 1562 | 1032 | 4 | 400 kV ×2; 230 kV ×2 | 11.9616 | L0014 L0015 L0175 L0366
Chennai South–Vellore (transport) | Chennai South | Vellore | AC | FALSE | 2584 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Chennai South–Vellore | 1552 | 1032 | 4 | 400 kV ×2; 230 kV ×2 | 11.2747 | L0023 L0024 L0291 L0479
Erode–Villupuram (transport) | Erode | Villupuram | AC | FALSE | 2290 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Erode–Villupuram | 1275 | 1015 | 3 | 400 kV ×2; 230 kV ×1 | 23.1628 | L0069 L0070 L0229
Coimbatore–Tirunelveli (transport) | Coimbatore | Tirunelveli | AC | FALSE | 1962 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Coimbatore–Tirunelveli | 981 | 981 | 2 | 400 kV ×2 | 40.7676 | L0043 L0044
Tirunelveli–Vellore (transport) | Tirunelveli | Vellore | AC | FALSE | 1700 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Tirunelveli–Vellore | 850 | 850 | 2 | 400 kV ×2 | 47.0767 | L0005 L0006
Erode–Trichy (transport) | Erode | Trichy | AC | FALSE | 1300 | -1 | 1 | 0 | 0 | inter-area (TN) transport alternative | both | Erode–Trichy | 1040 | 260 | 5 | 230 kV ×5 | 9.347 | L0161 L0187 L0422 L0423 L0437

## buses
name | v_nom | x | y | kind | within_area_mw | within_area_circuits
Tirunelveli | 400 | 77.721 | 8.947 | TN balancing area | 57993 | 85
Villupuram | 400 | 79.265 | 12.006 | TN balancing area | 17444 | 30
Chennai North | 400 | 79.929 | 13.201 | TN balancing area | 29276 | 63
Coimbatore | 400 | 77.064 | 10.956 | TN balancing area | 30706 | 58
Madurai | 400 | 78.114 | 9.939 | TN balancing area | 11221 | 26
Chennai South | 400 | 79.918 | 12.656 | TN balancing area | 11289 | 36
Trichy | 400 | 78.947 | 10.752 | TN balancing area | 8452 | 27
Vellore | 400 | 78.438 | 12.473 | TN balancing area | 8070 | 21
Erode | 400 | 77.852 | 11.495 | TN balancing area | 7340 | 28
Andhra Pradesh | 400 | 79.55 | 13.75 | neighbouring state
Karnataka | 400 | 77.25 | 12.85 | neighbouring state
Kerala | 400 | 76.75 | 9.75 | neighbouring state
Puducherry | 400 | 80.17 | 11.93 | neighbouring state
Western Region | 400 | 76.55 | 14.05 | neighbouring region

## lines
name | bus0 | bus1 | x | r | b | s_nom | s_max_pu | length | carrier | kind | s_nom_n1 | largest_circuit_mw | n_circuits | n_circuits_rated | circuits_by_kv | mw_by_kv | line_ids
Madurai–Tirunelveli | Madurai | Tirunelveli | 2.4215 | 0.2499 | 0.0060768 | 17462 | 0.7 | 113.9 | AC | inter-area (TN) | 15418 | 2044 | 23 | 23 | 400 kV ×8; 230 kV ×15 | 400 kV: 13482; 230 kV: 3980 | L0034 L0035 L0078 L0079 L0102 L0103 L0106 L0107 L0188 L0195 L0215 L0216 L0218 L0221 L0223 L0284 L0285 L0286 L0312 L0316 L0425 L0428 L0495
Vellore–Villupuram | Vellore | Villupuram | 4.5613 | 0.264 | 0.0078282 | 14070 | 0.7 | 160.7 | AC | inter-area (TN) | 8832 | 5238 | 6 | 6 | 765 kV ×2; 400 kV ×2; 230 kV ×2 | 765 kV: 10476; 400 kV: 3074; 230 kV: 520 | L0003 L0004 L0199 L0454 L0529 L0545
Madurai–Trichy | Madurai | Trichy | 4.0957 | 0.4224 | 0.0042992 | 11432 | 0.7 | 110.9 | AC | inter-area (TN) | 9388 | 2044 | 12 | 12 | 400 kV ×7; 230 kV ×5 | 400 kV: 10122; 230 kV: 1310 | L0032 L0033 L0083 L0084 L0108 L0109 L0110 L0169 L0292 L0293 L0301 L0435
Erode–Vellore | Erode | Vellore | 2.8726 | 0.2158 | 0.0023539 | 11266 | 0.7 | 88.8 | AC | inter-area (TN) | 9222 | 2044 | 10 | 10 | 400 kV ×6; 230 kV ×4 | 400 kV: 10206; 230 kV: 1060 | L0063 L0064 L0065 L0066 L0118 L0119 L0249 L0360 L0373 L0443
Trichy–Villupuram | Trichy | Villupuram | 5.5651 | 0.6148 | 0.0056243 | 9612 | 0.7 | 147.4 | AC | inter-area (TN) | 7894 | 1718 | 11 | 11 | 400 kV ×7; 230 kV ×4 | 400 kV: 8562; 230 kV: 1050 | L0052 L0060 L0061 L0085 L0086 L0125 L0231 L0266 L0267 L0465 L0518
Chennai North–Villupuram | Chennai North | Villupuram | 9.5062 | 0.457 | 0.009062 | 8416 | 0.7 | 272.5 | AC | inter-area (TN) | 4208 | 4208 | 2 | 2 | 765 kV ×2 | 765 kV: 8416 | L0525 L0527
Chennai North–Chennai South | Chennai North | Chennai South | 1.9446 | 0.2683 | 0.0023128 | 8282 | 0.7 | 60.3 | AC | inter-area (TN) | 7250 | 1032 | 15 | 14 | 400 kV ×6; 230 kV ×9 | 400 kV: 6192; 230 kV: 2090 | L0025 L0026 L0093 L0094 L0129 L0273 L0275 L0280 L0338 L0341 L0388 L0462 L0463 L0470 L0544
Coimbatore–Vellore | Coimbatore | Vellore | 9.749 | 0.5655 | 0.0070918 | 8204 | 0.7 | 258 | AC | inter-area (TN) | 6541 | 1663 | 6 | 6 | 400 kV ×6 | 400 kV: 8204 | L0058 L0059 L0121 L0122 L0123 L0124
Coimbatore–Erode | Coimbatore | Erode | 4.6355 | 0.656 | 0.0024265 | 6224 | 0.7 | 83.8 | AC | inter-area (TN) | 5192 | 1032 | 12 | 12 | 400 kV ×4; 230 kV ×8 | 400 kV: 4094; 230 kV: 2130 | L0067 L0068 L0116 L0117 L0202 L0206 L0237 L0255 L0257 L0305 L0309 L0421
Chennai South–Villupuram | Chennai South | Villupuram | 9.1087 | 1.2342 | 0.0024238 | 5247 | 0.7 | 124.4 | AC | inter-area (TN) | 3539 | 1708 | 9 | 9 | 400 kV ×2; 230 kV ×7 | 400 kV: 3407; 230 kV: 1840 | L0099 L0147 L0148 L0168 L0197 L0198 L0505 L0506 L0517
Coimbatore–Trichy | Coimbatore | Trichy | 4.6827 | 0.2716 | 0.00033901 | 4088 | 0.7 | 37 | AC | inter-area (TN) | 2044 | 2044 | 2 | 2 | 400 kV ×2 | 400 kV: 4088 | L0520 L0522
Coimbatore–Madurai | Coimbatore | Madurai | 14.2239 | 1.505 | 0.0018651 | 3339 | 0.7 | 141.2 | AC | inter-area (TN) | 2307 | 1032 | 4 | 4 | 400 kV ×3; 230 kV ×1 | 400 kV: 3079; 230 kV: 260 | L0038 L0095 L0096 L0386
Chennai North–Vellore | Chennai North | Vellore | 11.9616 | 1.4417 | 0.00097511 | 2594 | 0.7 | 90.2 | AC | inter-area (TN) | 1562 | 1032 | 4 | 4 | 400 kV ×2; 230 kV ×2 | 400 kV: 2064; 230 kV: 530 | L0014 L0015 L0175 L0366
Chennai South–Vellore | Chennai South | Vellore | 11.2747 | 1.4286 | 0.00095873 | 2584 | 0.7 | 83 | AC | inter-area (TN) | 1552 | 1032 | 4 | 4 | 400 kV ×2; 230 kV ×2 | 400 kV: 2064; 230 kV: 520 | L0023 L0024 L0291 L0479
Erode–Villupuram | Erode | Villupuram | 23.1628 | 2.5506 | 0.0013152 | 2290 | 0.7 | 148 | AC | inter-area (TN) | 1275 | 1015 | 3 | 3 | 400 kV ×2; 230 kV ×1 | 400 kV: 2030; 230 kV: 260 | L0069 L0070 L0229
Coimbatore–Tirunelveli | Coimbatore | Tirunelveli | 40.7676 | 3.816 | 0.0019941 | 1962 | 0.7 | 265 | AC | inter-area (TN) | 981 | 981 | 2 | 2 | 400 kV ×2 | 400 kV: 1962 | L0043 L0044
Tirunelveli–Vellore | Tirunelveli | Vellore | 47.0767 | 2.2631 | 0.0033544 | 1700 | 0.7 | 369 | AC | inter-area (TN) | 850 | 850 | 2 | 2 | 400 kV ×2 | 400 kV: 1700 | L0005 L0006
Erode–Trichy | Erode | Trichy | 9.347 | 1.7529 | 0.00023086 | 1300 | 0.7 | 47.6 | AC | inter-area (TN) | 1040 | 260 | 5 | 5 | 230 kV ×5 | 230 kV: 1300 | L0161 L0187 L0422 L0423 L0437

## circuits
line_id | ba_from | ba_to | frm | to | from_name | to_name | kv | kv_design | type | circuit | tower | conductor | length_km | capacity_mw | limit | thermal_mw | stability_mw | r_pu_km | x_pu_km | b_pu_km | r_ohm | x_ohm | b_siemens | rated | length_estimated | owner | status | source | note | cap_note
L0514 | Chennai North | Andhra Pradesh | SULLURPETA | GUMMIDIPOONDI | Sullurpeta 220 | Gummidipoondi | 220 | 220 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 49 | 249 | thermal | 249 | 1237 | 0.0001547 | 0.0008249 | 0.00142 | 12.1285 | 64.6722 | 4.3487e-05 | TRUE | FALSE | APTRANSCO+TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 1191 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0025 | Chennai North | Chennai South | KALIVANTHAPATU | VALLUR | Kalivandapattu 400/230 | Vallur TPS (NTECL) 400 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 134 | 1032 | thermal | 1032 | 1940 | 1.8e-05 | 0.0001923 | 0.00602 | 3.8592 | 41.2291 | 0.00050418 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 179
L0026 | Chennai North | Chennai South | KALIVANTHAPATU | VALLUR | Kalivandapattu 400/230 | Vallur TPS (NTECL) 400 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 134 | 1032 | thermal | 1032 | 1940 | 1.8e-05 | 0.0001923 | 0.00602 | 3.8592 | 41.2291 | 0.00050418 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 180
L0093 | Chennai North | Chennai South | ALAMATHI | S V CHATHRAM | Alamathi 400/230 | Sunguvarchatram 400/230 | 400 | 400 | AC | 1 | M/C | TWIN ACSR MOOSE | 47 | 1032 | thermal | 1032 | 5532 | 1.8e-05 | 0.0001923 | 0.00602 | 1.3536 | 14.461 | 0.00017684 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 339
L0094 | Chennai North | Chennai South | ALAMATHI | S V CHATHRAM | Alamathi 400/230 | Sunguvarchatram 400/230 | 400 | 400 | AC | 2 | M/C | TWIN ACSR MOOSE | 47 | 1032 | thermal | 1032 | 5532 | 1.8e-05 | 0.0001923 | 0.00602 | 1.3536 | 14.461 | 0.00017684 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 340
L0129 | Chennai North | Chennai South | S V CHATHRAM | NCTPS STG2 | Sunguvarchatram 400/230 | North Chennai TPS St-II 400 | 400 | 400 | AC | 1 | M/C | TWIN ACSR MOOSE | 95 | 1032 | thermal | 1032 | 2737 | 1.8e-05 | 0.0001923 | 0.00602 | 2.736 | 29.2296 | 0.00035744 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 377
L0544 | Chennai North | Chennai South | S V CHATHRAM | ENNORE SEZ | Sunguvarchatram 400/230 | Ennore SEZ 400 | 400 | 400 | AC | 1 | M/C | TWIN ACSR MOOSE | 77.821 | 1032 | thermal | 1032 | 3341 | 1.8e-05 | 0.0001923 | 0.00602 | 2.2412 | 23.944 | 0.0002928 | TRUE | FALSE | TANTRANSCO | in service | SR Annual Compendium 2025-26 (SRLDC), Table 58 (LILO), 27-02-2026 | LILO section; which S.V.Chathram–NCTPS circuit was LILO'd is assumed (ckt-2)
L0273 | Chennai North | Chennai South | KADAPERI | ALANDUR | Kadaperi (Tambaram) | Alandur (CMRL) | 230 | 230 | AC | 1 | S/C | 1200SQMM UGC | 12 | [10 empty] | FALSE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 611 |  | underground cable; no tabulated parameters – capacity not computed
L0275 | Chennai North | Chennai South | KADAPERI | PORUR | Kadaperi (Tambaram) | Porur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 9 | 260 | thermal | 260 | 7361 | 0.00014154 | 0.00075473 | 0.001552 | 2.0382 | 10.8681 | 8.7301e-06 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 613 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0280 | Chennai North | Chennai South | KALIVANTHAPATU | TARAMANI | Kalivandapattu 400/230 | Tharamani 400/230 GIS | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 45 | 260 | thermal | 260 | 1472 | 0.00014154 | 0.00075473 | 0.001552 | 10.1909 | 54.3405 | 4.3651e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 618 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0338 | Chennai North | Chennai South | KORATTUR | SRIPERUMBUDUR | Korattur 400/230/110 | Sriperumbudur 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 30 | 260 | thermal | 260 | 2208 | 0.00014154 | 0.00075473 | 0.001552 | 6.7939 | 36.227 | 2.91e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 676
L0341 | Chennai North | Chennai South | KOYAMBEDU | SRIPERUMBUDUR | Koyambedu | Sriperumbudur 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + 1200SQMM UGC | 46 | 260 | thermal | 260 | 1440 | 0.00014154 | 0.00075473 | 0.001552 | 10.4174 | 55.548 | 4.4621e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 679 |  | underground cable; mixed sections: weakest (highest-resistance) conductor used for whole line; cable section present – overhead parameters used, cable rating may be lower
L0388 | Chennai North | Chennai South | NCTPS STG1 | SRIPERUMBUDUR | North Chennai TPS St-I 230 | Sriperumbudur 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 73 | 260 | thermal | 260 | 908 | 0.00014154 | 0.00075473 | 0.001552 | 16.5319 | 88.1523 | 7.0811e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 726
L0462 | Chennai North | Chennai South | SRIPERUMBUDUR | SURYA DEV | Sriperumbudur 400/230 | Surya Dev (industrial) | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 54 | 260 | thermal | 260 | 1227 | 0.00014154 | 0.00075473 | 0.001552 | 12.2291 | 65.2086 | 5.2381e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 800 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0463 | Chennai North | Chennai South | SRIPERUMBUDUR | TARAMANI | Sriperumbudur 400/230 | Tharamani 400/230 GIS | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 35 | 260 | thermal | 260 | 1893 | 0.00014154 | 0.00075473 | 0.001552 | 7.9263 | 42.2648 | 3.3951e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 801
L0470 | Chennai North | Chennai South | TARAMANI | KITZ | Tharamani 400/230 GIS | KITZ (Sholinganallur) | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 18 | 270 | thermal | 270 | 3693 | 0.00013175 | 0.00075208 | 0.0015411 | 3.7944 | 21.6598 | 1.7337e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 808 |  | S/C parameters used (D/C not tabulated)
L0014 | Chennai North | Vellore | ALAMATHI | THIRUVALAM-TN | Alamathi 400/230 | Thiruvalam (TN) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 112 | 1032 | thermal | 1032 | 2322 | 1.8e-05 | 0.0001923 | 0.00602 | 3.2256 | 34.4602 | 0.0004214 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 128
L0015 | Chennai North | Vellore | ALAMATHI | THIRUVALAM-TN | Alamathi 400/230 | Thiruvalam (TN) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 112 | 1032 | thermal | 1032 | 2322 | 1.8e-05 | 0.0001923 | 0.00602 | 3.2256 | 34.4602 | 0.0004214 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 129
L0175 | Chennai North | Vellore | ALAMATHI | MOSUR | Alamathi 400/230 | Mosur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 52 | 260 | thermal | 260 | 1274 | 0.00014154 | 0.00075473 | 0.001552 | 11.7762 | 62.7934 | 5.0441e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 513 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0366 | Chennai North | Vellore | MOSUR | ATHIPATU | Mosur | Athipattu 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 85 | 270 | thermal | 270 | 782 | 0.00013175 | 0.00075208 | 0.0015411 | 17.9181 | 102.2823 | 8.1871e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 704
L0525 | Chennai North | Villupuram | NORTH CHENNAI PS | ARIYALUR | North Chennai 765 kV PS | Ariyalur 765/400 | 765 | 765 | AC | 1 | D/C | HEXA ACSR ZEBRA | 272.54 | 4208 | stability (30°) | 5238 | 4208 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.91399 | 19.0124 | 0.004531 | TRUE | FALSE | TANTRANSCO | in service | SR Annual Compendium 2023-24 (SRLDC), Table 33 #26, 06-01-2024
L0527 | Chennai North | Villupuram | NORTH CHENNAI PS | ARIYALUR | North Chennai 765 kV PS | Ariyalur 765/400 | 765 | 765 | AC | 2 | D/C | HEXA ACSR ZEBRA | 272.54 | 4208 | stability (30°) | 5238 | 4208 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.91399 | 19.0124 | 0.004531 | TRUE | FALSE | TANTRANSCO | in service | SR Annual Compendium 2023-24 (SRLDC), Table 33 #25, 18-01-2024
L0020 | Chennai South | Andhra Pradesh | CHITTOOR | SRIPERUMBUDUR | Chittoor 400/220 (AP) | Sriperumbudur 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 95 | 1015 | thermal | 1015 | 2536 | 1.862e-05 | 0.0002075 | 0.00555 | 2.8302 | 31.54 | 0.00032953 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 135
L0045 | Chennai South | Andhra Pradesh | NELLORE-PG | SRIPERUMBUDUR | Nellore (PG/PS) 400 | Sriperumbudur 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 189 | 1032 | thermal | 1032 | 1376 | 1.8e-05 | 0.0001923 | 0.00602 | 5.4432 | 58.1515 | 0.00071111 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 216
L0046 | Chennai South | Andhra Pradesh | NELLORE-PG | SRIPERUMBUDUR | Nellore (PG/PS) 400 | Sriperumbudur 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 189 | 1032 | thermal | 1032 | 1376 | 1.8e-05 | 0.0001923 | 0.00602 | 5.4432 | 58.1515 | 0.00071111 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 217
L0030 | Chennai South | Karnataka | KOLAR-PG | SRIPERUMBUDUR | Kolar (PG) 400 / HVDC | Sriperumbudur 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 238 | 1032 | thermal | 1032 | 1092 | 1.8e-05 | 0.0001923 | 0.00602 | 6.8544 | 73.2278 | 0.00089548 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 186
L0062 | Chennai South | Puducherry | S V CHATHRAM | PONDY | Sunguvarchatram 400/230 | Pondicherry (PG) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 129 | 1015 | thermal | 1015 | 1868 | 1.862e-05 | 0.0002075 | 0.00555 | 3.8432 | 42.828 | 0.00044747 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 269
L0023 | Chennai South | Vellore | KALIVANTHAPATU | THIRUVALAM-PG | Kalivandapattu 400/230 | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 114 | 1032 | thermal | 1032 | 2281 | 1.8e-05 | 0.0001923 | 0.00602 | 3.2832 | 35.0755 | 0.00042892 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 177
L0024 | Chennai South | Vellore | KALIVANTHAPATU | THIRUVALAM-PG | Kalivandapattu 400/230 | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 114 | 1032 | thermal | 1032 | 2281 | 1.8e-05 | 0.0001923 | 0.00602 | 3.2832 | 35.0755 | 0.00042892 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 178
L0291 | Chennai South | Vellore | KANCHIPURAM | THIRUVALAM-TN | Kanchipuram | Thiruvalam (TN) 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 52 | 260 | thermal | 260 | 1274 | 0.00014154 | 0.00075473 | 0.001552 | 11.7762 | 62.7934 | 5.0441e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 629
L0479 | Chennai South | Vellore | THIRUVALAM 230/110 | KANCHIPURAM | Thiruvalam (TN) 230/110 | Kanchipuram | 230 | 230 | AC | 1 | D/C | SINGLE ACSR KUNDAH | 52 | 260 | thermal | 260 | 1274 | 0.00014154 | 0.00075473 | 0.001552 | 11.7762 | 62.7934 | 5.0441e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 817 |  | S/C parameters used (D/C not tabulated)
L0099 | Chennai South | Villupuram | KALIVANTHAPATU | ARIYALUR | Kalivandapattu 400/230 | Ariyalur 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 186 | 1699 | stability (30°) | 2044 | 1699 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7311 | 47.0803 | 0.00085211 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 345
L0517 | Chennai South | Villupuram | KALIVANTHAPATU | ARIYALUR | Kalivandapattu 400/230 | Ariyalur 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 185 | 1708 | stability (30°) | 2044 | 1708 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7164 | 46.8272 | 0.00084753 | TRUE | FALSE | TANTRANSCO | in service | SR Annual Compendium 2023-24 (SRLDC), Table 34 #17 (LILO), 12-02-2024
L0147 | Chennai South | Villupuram | ARANI | BHAVINI | Arani | BHAVINI PFBR Kalpakkam | 230 | 230 | AC | 1 | D/C | SINGLE AAAC ZEBRA | 106 | 260 | thermal | 260 | 625 | 0.00014154 | 0.00075473 | 0.001552 | 24.0052 | 128.002 | 0.00010282 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 485 |  | S/C parameters used (D/C not tabulated)
L0148 | Chennai South | Villupuram | ARANI | BHAVINI | Arani | BHAVINI PFBR Kalpakkam | 230 | 230 | AC | 2 | D/C | SINGLE AAAC ZEBRA | 106 | 260 | thermal | 260 | 625 | 0.00014154 | 0.00075473 | 0.001552 | 24.0052 | 128.002 | 0.00010282 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 486 |  | S/C parameters used (D/C not tabulated)
L0168 | Chennai South | Villupuram | ACHARAPAKKAM | VILLUPURAM | Acharapakkam | Villupuram | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 72 | 260 | thermal | 260 | 920 | 0.00014154 | 0.00075473 | 0.001552 | 16.3054 | 86.9448 | 6.9841e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 506
L0197 | Chennai South | Villupuram | ARANI | ECHUR | Arani | Echur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 46 | 260 | thermal | 260 | 1440 | 0.00014154 | 0.00075473 | 0.001552 | 10.4174 | 55.548 | 4.4621e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 535 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0198 | Chennai South | Villupuram | ARANI | KANCHIPURAM | Arani | Kanchipuram | 230 | 230 | AC | 2 | S/C | SINGLE ACSR KUNDAH | 63 | 260 | thermal | 260 | 1052 | 0.00014154 | 0.00075473 | 0.001552 | 14.2673 | 76.0767 | 6.1111e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 536
L0505 | Chennai South | Villupuram | VEERAPURAM | CUDDALORE | Veerapuram | Cuddalore | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 178 | 270 | thermal | 270 | 373 | 0.00013175 | 0.00075208 | 0.0015411 | 37.5225 | 214.1911 | 0.00017145 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 843 |  | S/C parameters used (D/C not tabulated)
L0506 | Chennai South | Villupuram | VEERAPURAM | CUDDALORE | Veerapuram | Cuddalore | 230 | 230 | AC | 2 | D/C | SINGLE ACSR ZEBRA | 178 | 270 | thermal | 270 | 373 | 0.00013175 | 0.00075208 | 0.0015411 | 37.5225 | 214.1911 | 0.00017145 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 844 |  | S/C parameters used (D/C not tabulated)
L0067 | Coimbatore | Erode | SALEM-PG | MYWADI | Salem (PG) 400/230 | Udumalpet / Mywadi (PG) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 150 | 1015 | thermal | 1015 | 1606 | 1.862e-05 | 0.0002075 | 0.00555 | 4.4688 | 49.8 | 0.00052031 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 274
L0068 | Coimbatore | Erode | SALEM-PG | MYWADI | Salem (PG) 400/230 | Udumalpet / Mywadi (PG) 400/230 | 400 | 400 | AC | 2 | S/C | TWIN ACSR MOOSE | 150 | 1015 | thermal | 1015 | 1606 | 1.862e-05 | 0.0002075 | 0.00555 | 4.4688 | 49.8 | 0.00052031 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 275
L0116 | Coimbatore | Erode | MTPS-3 | KARAMADAI | Mettur TPS St-III 400/230 | Karamadai 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 126 | 1032 | thermal | 1032 | 2064 | 1.8e-05 | 0.0001923 | 0.00602 | 3.6288 | 38.7677 | 0.00047408 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 364
L0117 | Coimbatore | Erode | MTPS-3 | KARAMADAI | Mettur TPS St-III 400/230 | Karamadai 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 126 | 1032 | thermal | 1032 | 2064 | 1.8e-05 | 0.0001923 | 0.00602 | 3.6288 | 38.7677 | 0.00047408 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 365
L0202 | Coimbatore | Erode | ARASUR | GOBI | Arasur (TN) | Gobichettipalayam | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 80 | 260 | thermal | 260 | 828 | 0.00014154 | 0.00075473 | 0.001552 | 18.1172 | 96.6053 | 7.7601e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 540
L0206 | Coimbatore | Erode | ARASUR | SHENBAGAPUDUR | Arasur (TN) | Shenbagapudur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 66 | 270 | thermal | 270 | 1007 | 0.00013175 | 0.00075208 | 0.0015411 | 13.9128 | 79.4192 | 6.357e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 544
L0237 | Coimbatore | Erode | GOBI | ARASUR | Gobichettipalayam | Arasur (TN) | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 55 | 270 | thermal | 270 | 1209 | 0.00013175 | 0.00075208 | 0.0015411 | 11.594 | 66.1827 | 5.2975e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 575
L0255 | Coimbatore | Erode | INGUR | ARASUR | Ingur | Arasur (TN) | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 54 | 270 | thermal | 270 | 1231 | 0.00013175 | 0.00075208 | 0.0015411 | 11.3832 | 64.9793 | 5.2012e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 593 |  | S/C parameters used (D/C not tabulated)
L0257 | Coimbatore | Erode | INGUR | KARAMADAI | Ingur | Karamadai 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 67 | 260 | thermal | 260 | 989 | 0.00014154 | 0.00075473 | 0.001552 | 15.1731 | 80.9069 | 6.4991e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 595 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0305 | Coimbatore | Erode | KARAMADAI | SHENBAGAPUDUR | Karamadai 400/230 | Shenbagapudur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 40 | 270 | thermal | 270 | 1662 | 0.00013175 | 0.00075208 | 0.0015411 | 8.432 | 48.1328 | 3.8527e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 643
L0309 | Coimbatore | Erode | KARUVALUR | SHENBAGAPUDUR | Karuvalur | Shenbagapudur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 37 | 270 | thermal | 270 | 1797 | 0.00013175 | 0.00075208 | 0.0015411 | 7.7996 | 44.5229 | 3.5638e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 647
L0421 | Coimbatore | Erode | PARAMATHY | KURKATHI | Paramathi | Kurkathi | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 54 | 260 | thermal | 260 | 1227 | 0.00014154 | 0.00075473 | 0.001552 | 12.2291 | 65.2086 | 5.2381e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 759 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0039 | Coimbatore | Kerala | MYWADI | PALAKKAD-PG | Udumalpet / Mywadi (PG) 400/230 | Palakkad (PG) 400/220 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 96 | 1032 | thermal | 1032 | 2708 | 1.8e-05 | 0.0001923 | 0.00602 | 2.7648 | 29.5373 | 0.0003612 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 198
L0040 | Coimbatore | Kerala | MYWADI | PALAKKAD-PG | Udumalpet / Mywadi (PG) 400/230 | Palakkad (PG) 400/220 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 96 | 1032 | thermal | 1032 | 2708 | 1.8e-05 | 0.0001923 | 0.00602 | 2.7648 | 29.5373 | 0.0003612 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 199
L0549 | Coimbatore | Kerala | PUGALUR HVDC | TRICHUR HVDC | Pugalur HVDC ±800 kV / VSC terminal | Thrissur (Madakkathara) VSC HVDC | 320 | 320 | HVDC | Bipole |  | TWIN ACSR LAPWING + UGC | 165 | 2000 | converter rating | [8 empty] | TRUE | FALSE | POWERGRID | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row HVDC table 11-12 | ±320 kV VSC, 2 × 1000 MW, 165 km incl. underground cable (2023 compendium HVDC table, rows 11-12) | HVDC: rated converter capacity
L0139 | Coimbatore | Kerala | UDUMALPET | PALLIVASAL | Udumalpet (TN) 230 | Pallivasal 220 | 230 | 230 | AC | 1 | D/C | SINGLE ACSR KUNDAH | 67 | 260 | thermal | 260 | 989 | 0.00014154 | 0.00075473 | 0.001552 | 15.1731 | 80.9069 | 6.4991e-05 | TRUE | FALSE | KSEB | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 477 |  | S/C parameters used (D/C not tabulated)
L0038 | Coimbatore | Madurai | MYWADI | MADURAI-PG | Udumalpet / Mywadi (PG) 400/230 | Madurai (PG) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 127 | 1015 | thermal | 1015 | 1897 | 1.862e-05 | 0.0002075 | 0.00555 | 3.7836 | 42.164 | 0.00044053 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 197
L0095 | Coimbatore | Madurai | ANAIKADAVU | THAPAKUNDU | Anaikadavu 400/230 | Thappagundu 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 179 | 1032 | thermal | 1032 | 1453 | 1.8e-05 | 0.0001923 | 0.00602 | 5.1552 | 55.0747 | 0.00067349 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 341
L0096 | Coimbatore | Madurai | ANAIKADAVU | THAPAKUNDU | Anaikadavu 400/230 | Thappagundu 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 179 | 1032 | thermal | 1032 | 1453 | 1.8e-05 | 0.0001923 | 0.00602 | 5.1552 | 55.0747 | 0.00067349 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 342
L0386 | Coimbatore | Madurai | MYWADI | SEMPATTI | Udumalpet / Mywadi (PG) 400/230 | Sempatti | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 80 | 260 | thermal | 260 | 828 | 0.00014154 | 0.00075473 | 0.001552 | 18.1172 | 96.6053 | 7.7601e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 724
L0043 | Coimbatore | Tirunelveli | MYWADI | TIRUNELVELI-PG | Udumalpet / Mywadi (PG) 400/230 | Tirunelveli (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 265 | 981 | stability (30°) | 1032 | 981 | 1.8e-05 | 0.0001923 | 0.00602 | 7.632 | 81.5352 | 0.00099706 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 202
L0044 | Coimbatore | Tirunelveli | MYWADI | TIRUNELVELI-PG | Udumalpet / Mywadi (PG) 400/230 | Tirunelveli (PG) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 265 | 981 | stability (30°) | 1032 | 981 | 1.8e-05 | 0.0001923 | 0.00602 | 7.632 | 81.5352 | 0.00099706 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 203
L0520 | Coimbatore | Trichy | KARUR PS | PUGALUR-PG | Karur ISTS pooling station 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 37 | 2044 | thermal | 2044 | 8542 | 9.177e-06 | 0.0001582 | 0.00733 | 0.54328 | 9.3654 | 0.00016951 | TRUE | FALSE | Karur Transmission Ltd | in service | SR Annual Compendium 2023-24 (SRLDC), Table 34 #14 (LILO), 24-10-2023
L0522 | Coimbatore | Trichy | KARUR PS | PUGALUR-PG | Karur ISTS pooling station 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 37 | 2044 | thermal | 2044 | 8542 | 9.177e-06 | 0.0001582 | 0.00733 | 0.54328 | 9.3654 | 0.00016951 | TRUE | FALSE | Karur Transmission Ltd | in service | SR Annual Compendium 2023-24 (SRLDC), Table 34 #13 (LILO), 24-10-2023
L0058 | Coimbatore | Vellore | PUGALUR HVDC | THIRUVALAM-PG | Pugalur HVDC ±800 kV / VSC terminal | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 390 | 810 | stability (30°) | 2044 | 810 | 9.177e-06 | 0.0001582 | 0.00733 | 5.7264 | 98.7168 | 0.0017867 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 253
L0059 | Coimbatore | Vellore | PUGALUR HVDC | THIRUVALAM-PG | Pugalur HVDC ±800 kV / VSC terminal | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 390 | 810 | stability (30°) | 2044 | 810 | 9.177e-06 | 0.0001582 | 0.00733 | 5.7264 | 98.7168 | 0.0017867 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 254
L0121 | Coimbatore | Vellore | PALAVADI | RASIPALAYAM | Palavadi 400/230 | Rasipalayam 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 194 | 1629 | stability (30°) | 2044 | 1629 | 9.177e-06 | 0.0001582 | 0.00733 | 2.8485 | 49.1053 | 0.00088876 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 369
L0122 | Coimbatore | Vellore | PALAVADI | RASIPALAYAM | Palavadi 400/230 | Rasipalayam 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 194 | 1629 | stability (30°) | 2044 | 1629 | 9.177e-06 | 0.0001582 | 0.00733 | 2.8485 | 49.1053 | 0.00088876 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 370
L0123 | Coimbatore | Vellore | PALAVADI | RASIPALAYAM | Palavadi 400/230 | Rasipalayam 400/230 | 400 | 400 | AC | 3 | D/C | QUAD ACSR MOOSE | 190 | 1663 | stability (30°) | 2044 | 1663 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7898 | 48.0928 | 0.00087044 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 371
L0124 | Coimbatore | Vellore | PALAVADI | RASIPALAYAM | Palavadi 400/230 | Rasipalayam 400/230 | 400 | 400 | AC | 4 | D/C | QUAD ACSR MOOSE | 190 | 1663 | stability (30°) | 2044 | 1663 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7898 | 48.0928 | 0.00087044 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 372
L0548 | Coimbatore | Western Region | RAIGARH HVDC | PUGALUR HVDC | Raigarh (Kotra) HVDC ±800 kV | Pugalur HVDC ±800 kV / VSC terminal | 800 | 800 | HVDC | Bipole | D/C | HEXA ACSR LAPWING | 1765 | 6000 | converter rating | [8 empty] | TRUE | FALSE | POWERGRID | in service | SR Annual Compendium 2025-26 (SRLDC), Table 8 #13-14 | ±800 kV LCC, 4 × 1500 MW (2023 compendium HVDC table, rows 7-10); inter-regional WR–SR; 2025-26: 18,558 MU import / 945 MU export | HVDC: rated converter capacity
L0161 | Erode | Trichy | PARAMATHY | SPRING-PGLR | Paramathi | Spring Akshaya wind (Pugalur) | 230 | 230 | AC | 1 | S/C | SINGLE ACSR MOOSE | 34 | 260 | thermal | 260 | 1948 | 0.00014154 | 0.00075473 | 0.001552 | 7.6998 | 41.0573 | 3.2981e-05 | TRUE | FALSE | SPRING-PGLR | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 499
L0187 | Erode | Trichy | ALUNDUR | VALAYAPATTY | Alundur (Trichy) | Valayapatti | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 90 | 260 | thermal | 260 | 736 | 0.00014154 | 0.00075473 | 0.001552 | 20.3818 | 108.681 | 8.7301e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 525
L0422 | Erode | Trichy | PARAMATHY | PUGALUR | Paramathi | Pugalur (TN) 230 | 230 | 230 | AC | 1 | D/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 28 | 260 | thermal | 260 | 2366 | 0.00014154 | 0.00075473 | 0.001552 | 6.341 | 33.8119 | 2.716e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 760 |  | S/C parameters used (D/C not tabulated); mixed sections: weakest (highest-resistance) conductor used for whole line
L0423 | Erode | Trichy | PARAMATHY | PUGALUR | Paramathi | Pugalur (TN) 230 | 230 | 230 | AC | 2 | D/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 28 | 260 | thermal | 260 | 2366 | 0.00014154 | 0.00075473 | 0.001552 | 6.341 | 33.8119 | 2.716e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 761 |  | S/C parameters used (D/C not tabulated); mixed sections: weakest (highest-resistance) conductor used for whole line
L0437 | Erode | Trichy | PUTHANSANTHAI | PUGALUR | Puthanchandai | Pugalur (TN) 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 58 | 260 | thermal | 260 | 1142 | 0.00014154 | 0.00075473 | 0.001552 | 13.1349 | 70.0388 | 5.6261e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 775 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0063 | Erode | Vellore | SALEM-PG | DHARAMAPURI | Salem (PG) 400/230 | Dharmapuri (Salem PS) 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 59 | 2044 | thermal | 2044 | 5357 | 9.177e-06 | 0.0001582 | 0.00733 | 0.86631 | 14.9341 | 0.00027029 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 270
L0064 | Erode | Vellore | SALEM-PG | DHARAMAPURI | Salem (PG) 400/230 | Dharmapuri (Salem PS) 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 59 | 2044 | thermal | 2044 | 5357 | 9.177e-06 | 0.0001582 | 0.00733 | 0.86631 | 14.9341 | 0.00027029 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 271
L0065 | Erode | Vellore | SALEM-PG | HOSUR-PG | Salem (PG) 400/230 | Hosur (PG) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 126 | 1015 | thermal | 1015 | 1912 | 1.862e-05 | 0.0002075 | 0.00555 | 3.7538 | 41.832 | 0.00043706 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 272
L0066 | Erode | Vellore | SALEM-PG | HOSUR-PG | Salem (PG) 400/230 | Hosur (PG) 400/230 | 400 | 400 | AC | 2 | S/C | TWIN ACSR MOOSE | 125 | 1015 | thermal | 1015 | 1928 | 1.862e-05 | 0.0002075 | 0.00555 | 3.724 | 41.5 | 0.00043359 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 273
L0118 | Erode | Vellore | MTPS-3 | PALAVADI | Mettur TPS St-III 400/230 | Palavadi 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 61 | 2044 | thermal | 2044 | 5181 | 9.177e-06 | 0.0001582 | 0.00733 | 0.89568 | 15.4403 | 0.00027946 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 366
L0119 | Erode | Vellore | MTPS-3 | PALAVADI | Mettur TPS St-III 400/230 | Palavadi 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 61 | 2044 | thermal | 2044 | 5181 | 9.177e-06 | 0.0001582 | 0.00733 | 0.89568 | 15.4403 | 0.00027946 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 367
L0249 | Erode | Vellore | HOSUR | METTUR AUTO | Hosur (TN) 230 | Mettur Auto 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 135 | 270 | thermal | 270 | 492 | 0.00013175 | 0.00075208 | 0.0015411 | 28.4581 | 162.4483 | 0.00013003 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 587
L0360 | Erode | Vellore | METTUR AUTO | PALAVADI | Mettur Auto 230 | Palavadi 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 56 | 270 | thermal | 270 | 1187 | 0.00013175 | 0.00075208 | 0.0015411 | 11.8048 | 67.386 | 5.3938e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 698
L0373 | Erode | Vellore | MTPS | SINGARAPET | Mettur TPS St-I/II 230 | Singarapettai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 110 | 260 | thermal | 260 | 602 | 0.00014154 | 0.00075473 | 0.001552 | 24.9111 | 132.8323 | 0.0001067 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 711
L0443 | Erode | Vellore | SALEM | SINGARAPET | Salem (TN) 230 | Singarapettai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 96 | 260 | thermal | 260 | 690 | 0.00014154 | 0.00075473 | 0.001552 | 21.7406 | 115.9264 | 9.3121e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 781
L0069 | Erode | Villupuram | SALEM-PG | NLC STG2 | Salem (PG) 400/230 | NLC TPS-II 400/230 | 400 | 400 | AC | 2 | S/C | TWIN ACSR MOOSE | 175 | 1015 | thermal | 1015 | 1377 | 1.862e-05 | 0.0002075 | 0.00555 | 5.2136 | 58.1 | 0.00060703 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 276
L0070 | Erode | Villupuram | SALEM-PG | NNTPP | Salem (PG) 400/230 | New Neyveli TPS (NNTPP) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 179 | 1015 | thermal | 1015 | 1346 | 1.862e-05 | 0.0002075 | 0.00555 | 5.3328 | 59.428 | 0.00062091 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 277
L0229 | Erode | Villupuram | DEVIYAKURICHI | STCMS | Deviyakurichi | ST-CMS Neyveli | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 90 | 260 | thermal | 260 | 736 | 0.00014154 | 0.00075473 | 0.001552 | 20.3818 | 108.681 | 8.7301e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 567
L0510 | Madurai | Kerala | THENI | SABARIGIRI | Theni 230 | Sabarigiri (Moozhiyar) 220 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 133 | 260 | thermal | 260 | 498 | 0.00014154 | 0.00075473 | 0.001552 | 30.1198 | 160.6063 | 0.00012901 | TRUE | FALSE | TANTRANSCO+KSEB | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 848
L0034 | Madurai | Tirunelveli | MADURAI-PG | TUTICORIN-PS | Madurai (PG) 400/230 | Tuticorin PS 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 95 | 2044 | thermal | 2044 | 3327 | 9.177e-06 | 0.0001582 | 0.00733 | 1.3949 | 24.0464 | 0.00043522 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 190
L0035 | Madurai | Tirunelveli | MADURAI-PG | TUTICORIN-PS | Madurai (PG) 400/230 | Tuticorin PS 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 95 | 2044 | thermal | 2044 | 3327 | 9.177e-06 | 0.0001582 | 0.00733 | 1.3949 | 24.0464 | 0.00043522 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 191
L0078 | Madurai | Tirunelveli | TIRUNELVELI-PG | MADURAI-PG | Tirunelveli (PG) 400/230 | Madurai (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 162 | 1032 | thermal | 1032 | 1605 | 1.8e-05 | 0.0001923 | 0.00602 | 4.6656 | 49.8442 | 0.00060952 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 305
L0079 | Madurai | Tirunelveli | TIRUNELVELI-PG | MADURAI-PG | Tirunelveli (PG) 400/230 | Madurai (PG) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 162 | 1032 | thermal | 1032 | 1605 | 1.8e-05 | 0.0001923 | 0.00602 | 4.6656 | 49.8442 | 0.00060952 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 306
L0102 | Madurai | Tirunelveli | KAMUTHI | OTTAPIDARAM | Kamuthi 400/230 | Ottapidaram 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 75 | 2044 | thermal | 2044 | 4214 | 9.177e-06 | 0.0001582 | 0.00733 | 1.1012 | 18.984 | 0.00034359 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 349
L0103 | Madurai | Tirunelveli | KAMUTHI | OTTAPIDARAM | Kamuthi 400/230 | Ottapidaram 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 75 | 2044 | thermal | 2044 | 4214 | 9.177e-06 | 0.0001582 | 0.00733 | 1.1012 | 18.984 | 0.00034359 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 350
L0106 | Madurai | Tirunelveli | KARAIKUDI-PG | KAYATHAR | Karaikudi (PG) 400/230 | Kayathar 400/230/110 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 195 | 1621 | stability (30°) | 2044 | 1621 | 9.177e-06 | 0.0001582 | 0.00733 | 2.8632 | 49.3584 | 0.00089334 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 353
L0107 | Madurai | Tirunelveli | KARAIKUDI-PG | KAYATHAR | Karaikudi (PG) 400/230 | Kayathar 400/230/110 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 195 | 1621 | stability (30°) | 2044 | 1621 | 9.177e-06 | 0.0001582 | 0.00733 | 2.8632 | 49.3584 | 0.00089334 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 354
L0188 | Madurai | Tirunelveli | AMUDHAPURAM | CHECKANURANI | Amudhapuram | Checkanurani | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 112 | 270 | thermal | 270 | 594 | 0.00013175 | 0.00075208 | 0.0015411 | 23.6097 | 134.772 | 0.00010788 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 526
L0195 | Madurai | Tirunelveli | ANUPANKULAM | PASUMALAI | Anuppankulam | Pasumalai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 75 | 260 | thermal | 260 | 883 | 0.00014154 | 0.00075473 | 0.001552 | 16.9848 | 90.5675 | 7.2751e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 533
L0215 | Madurai | Tirunelveli | CHECKANURANI | IND BHARATH 2 | Checkanurani | Ind-Barath 2 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 134 | 270 | thermal | 270 | 496 | 0.00013175 | 0.00075208 | 0.0015411 | 28.2473 | 161.245 | 0.00012907 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 553
L0216 | Madurai | Tirunelveli | CHECKANURANI | KAYATHAR 230/110 | Checkanurani | Kayathar (old) 230/110 | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 148 | 270 | thermal | 270 | 449 | 0.00013175 | 0.00075208 | 0.0015411 | 31.1985 | 178.0915 | 0.00014255 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 554 |  | S/C parameters used (D/C not tabulated)
L0218 | Madurai | Tirunelveli | CHECKANURANI | NALLAMANAICKENPATTI | Checkanurani | Nallamanaickenpatti | 230 | 230 | AC | 2 | S/C | SINGLE ACSR ZEBRA | 85 | 270 | thermal | 270 | 782 | 0.00013175 | 0.00075208 | 0.0015411 | 17.9181 | 102.2823 | 8.1871e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 556
L0221 | Madurai | Tirunelveli | CHECKANURANI | SAVASPURAM | Checkanurani | Savaspuram | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 68 | 270 | thermal | 270 | 978 | 0.00013175 | 0.00075208 | 0.0015411 | 14.3345 | 81.8258 | 6.5497e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 559
L0223 | Madurai | Tirunelveli | CHECKANURANI | TTPS | Checkanurani | Tuticorin TPS 230 | 230 | 230 | AC | 2 | D/C | SINGLE ACSR KUNDAH | 148 | 260 | thermal | 260 | 448 | 0.00014154 | 0.00075473 | 0.001552 | 33.5167 | 178.7198 | 0.00014356 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 561 |  | S/C parameters used (D/C not tabulated)
L0284 | Madurai | Tirunelveli | KAMUTHI | TIRUCHULI | Kamuthi 400/230 | Tiruchuli | 230 | 230 | AC | 1 | D/C | SINGLE ACSR ZEBRA | 45 | 270 | thermal | 270 | 1477 | 0.00013175 | 0.00075208 | 0.0015411 | 9.486 | 54.1494 | 4.3343e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 622 |  | S/C parameters used (D/C not tabulated)
L0285 | Madurai | Tirunelveli | KAMUTHI | TIRUCHULI | Kamuthi 400/230 | Tiruchuli | 230 | 230 | AC | 2 | D/C | SINGLE ACSR ZEBRA | 45 | 270 | thermal | 270 | 1477 | 0.00013175 | 0.00075208 | 0.0015411 | 9.486 | 54.1494 | 4.3343e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 623 |  | S/C parameters used (D/C not tabulated)
L0286 | Madurai | Tirunelveli | KAMUTHI | TIRUCHULI | Kamuthi 400/230 | Tiruchuli | 230 | 230 | AC | 3 | D/C | SINGLE ACSR ZEBRA | 45 | 270 | thermal | 270 | 1477 | 0.00013175 | 0.00075208 | 0.0015411 | 9.486 | 54.1494 | 4.3343e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 624 |  | S/C parameters used (D/C not tabulated)
L0312 | Madurai | Tirunelveli | KAVANUR | MILAVITTAN | Kavanur | Milavittan | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 106 | 260 | thermal | 260 | 625 | 0.00014154 | 0.00075473 | 0.001552 | 24.0052 | 128.002 | 0.00010282 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 650 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0316 | Madurai | Tirunelveli | KAYATHAR 230/110 | KINNIMANGALAM | Kayathar (old) 230/110 | Kinnimangalam | 230 | 230 | AC | 2 | D/C | SINGLE ACSR KUNDAH | 148 | 260 | thermal | 260 | 448 | 0.00014154 | 0.00075473 | 0.001552 | 33.5167 | 178.7198 | 0.00014356 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 654 |  | S/C parameters used (D/C not tabulated)
L0425 | Madurai | Tirunelveli | PASUMALAI | KAYATHAR | Pasumalai | Kayathar 400/230/110 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 126 | 260 | thermal | 260 | 526 | 0.00014154 | 0.00075473 | 0.001552 | 28.5345 | 152.1534 | 0.00012222 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 763
L0428 | Madurai | Tirunelveli | PASUMALAI | TTPS | Pasumalai | Tuticorin TPS 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 138 | 260 | thermal | 260 | 480 | 0.00014154 | 0.00075473 | 0.001552 | 31.2521 | 166.6441 | 0.00013386 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 766
L0495 | Madurai | Tirunelveli | TTPS | KINNIMANGALAM | Tuticorin TPS 230 | Kinnimangalam | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 142 | 260 | thermal | 260 | 467 | 0.00014154 | 0.00075473 | 0.001552 | 32.1579 | 171.4744 | 0.00013774 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 833
L0032 | Madurai | Trichy | MADURAI-PG | PUGALUR-PG | Madurai (PG) 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 124 | 1032 | thermal | 1032 | 2097 | 1.8e-05 | 0.0001923 | 0.00602 | 3.5712 | 38.1523 | 0.00046655 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 188
L0033 | Madurai | Trichy | MADURAI-PG | PUGALUR-PG | Madurai (PG) 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 124 | 1032 | thermal | 1032 | 2097 | 1.8e-05 | 0.0001923 | 0.00602 | 3.5712 | 38.1523 | 0.00046655 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 189
L0083 | Madurai | Trichy | TRICHY-PG | KARAIKUDI-PG | Trichy (PG) 400/230 | Karaikudi (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 98 | 1032 | thermal | 1032 | 2653 | 1.8e-05 | 0.0001923 | 0.00602 | 2.8224 | 30.1526 | 0.00036872 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 316
L0084 | Madurai | Trichy | TRICHY-PG | MADURAI-PG | Trichy (PG) 400/230 | Madurai (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 130 | 1032 | thermal | 1032 | 2000 | 1.8e-05 | 0.0001923 | 0.00602 | 3.744 | 39.9984 | 0.00048913 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 317
L0108 | Madurai | Trichy | KARAIKUDI-PG | PUGALUR-PG | Karaikudi (PG) 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 160 | 1975 | stability (30°) | 2044 | 1975 | 9.177e-06 | 0.0001582 | 0.00733 | 2.3493 | 40.4992 | 0.000733 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 355
L0109 | Madurai | Trichy | KARAIKUDI-PG | PUGALUR-PG | Karaikudi (PG) 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 160 | 1975 | stability (30°) | 2044 | 1975 | 9.177e-06 | 0.0001582 | 0.00733 | 2.3493 | 40.4992 | 0.000733 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 356
L0110 | Madurai | Trichy | KARAIKUDI-PG | VELLALVDUTHI | Karaikudi (PG) 400/230 | Vellalaviduthi 400/230 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 145 | 2044 | thermal | 2044 | 2180 | 9.177e-06 | 0.0001582 | 0.00733 | 2.1291 | 36.7024 | 0.00066428 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 357
L0169 | Madurai | Trichy | ALAGAR KOVIL | MANDIPATTI | Alagarkovil | Mandipatti | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 105 | 260 | thermal | 260 | 631 | 0.00014154 | 0.00075473 | 0.001552 | 23.7788 | 126.7945 | 0.00010185 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 507 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0292 | Madurai | Trichy | KARAIKUDI 230/110 | KARAMBAYAM | Karaikudi (TN) 230/110 | Karambayam | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 88 | 260 | thermal | 260 | 753 | 0.00014154 | 0.00075473 | 0.001552 | 19.9289 | 106.2658 | 8.5361e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 630 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0293 | Madurai | Trichy | KARAIKUDI 230/110 | KARAMBAYAM | Karaikudi (TN) 230/110 | Karambayam | 230 | 230 | AC | 2 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 88 | 260 | thermal | 260 | 753 | 0.00014154 | 0.00075473 | 0.001552 | 19.9289 | 106.2658 | 8.5361e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 631 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0301 | Madurai | Trichy | KARAIKUDI-PG | PUDUKOTAI | Karaikudi (PG) 400/230 | Pudukkottai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 49 | 270 | thermal | 270 | 1357 | 0.00013175 | 0.00075208 | 0.0015411 | 10.3292 | 58.9627 | 4.7196e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 639
L0435 | Madurai | Trichy | PUGALUR | RENGANATHAPURAM | Pugalur (TN) 230 | Renganathapuram | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR ZEBRA | 60 | 260 | thermal | 260 | 1104 | 0.00014154 | 0.00075473 | 0.001552 | 13.5879 | 72.454 | 5.8201e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 773 |  | mixed sections: weakest (highest-resistance) conductor used for whole line
L0080 | Tirunelveli | Kerala | TIRUNELVELI-PG | TRIVANDRUM-PG | Tirunelveli (PG) 400/230 | Trivandrum (PG) 400/220 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 160 | 1032 | thermal | 1032 | 1625 | 1.8e-05 | 0.0001923 | 0.00602 | 4.608 | 49.2288 | 0.000602 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 307
L0081 | Tirunelveli | Kerala | TIRUNELVELI-PG | TRIVANDRUM-PG | Tirunelveli (PG) 400/230 | Trivandrum (PG) 400/220 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 160 | 1032 | thermal | 1032 | 1625 | 1.8e-05 | 0.0001923 | 0.00602 | 4.608 | 49.2288 | 0.000602 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 308
L0523 | Tirunelveli | Kerala | TIRUNELVELI-PG | KOTTAYAM | Tirunelveli (PG) 400/230 | Kottayam 400/220 GIS | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 188.21 | 1679 | stability (30°) | 2044 | 1679 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7635 | 47.6397 | 0.00086224 | TRUE | FALSE | PGCIL/KSEB | in service | SR Annual Compendium 2023-24 (SRLDC), Table 34 #2 (LILO), 13-05-2023
L0524 | Tirunelveli | Kerala | TIRUNELVELI-PG | KOTTAYAM | Tirunelveli (PG) 400/230 | Kottayam 400/220 GIS | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 188.2 | 1679 | stability (30°) | 2044 | 1679 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7634 | 47.6372 | 0.00086219 | TRUE | FALSE | PGCIL/KSEB | in service | SR Annual Compendium 2023-24 (SRLDC), Table 34 #3 (LILO), 21-09-2023
L0135 | Tirunelveli | Kerala | ABISHEKAPATTI | EDAMON | Abishekapatti 230 | Edamon 400/220 | 220 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 82 | 568 | thermal | 568 | 959 | 5.9504e-05 | 0.0006357 | 0.0018211 | 7.8069 | 83.4042 | 9.3329e-05 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 473 | Built for 400 kV, operated at 220 kV (2023)
L0136 | Tirunelveli | Kerala | ABISHEKAPATTI | EDAMON | Abishekapatti 230 | Edamon 400/220 | 220 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 82 | 568 | thermal | 568 | 959 | 5.9504e-05 | 0.0006357 | 0.0018211 | 7.8069 | 83.4042 | 9.3329e-05 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 474 | Built for 400 kV, operated at 220 kV (2023)
L0516 | Tirunelveli | Kerala | KUZHITHURAI | PARASSALA | Kuzhithurai 110 | Parassala 110 | 110 | 110 | AC | 1 | D/C | SINGLE ACSR MINK | 5 | [10 empty] | FALSE | FALSE | TANTRANSCO+KSEB | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 2018 |  | 1xACSR MINK at 110 kV not in parameter table; no tabulated parameters – capacity not computed
L0005 | Tirunelveli | Vellore | DHARAMAPURI | TUTICORIN-PS | Dharmapuri (Salem PS) 765/400 | Tuticorin PS 765/400 | 400 | 765 | AC | 1 | D/C | HEXA ACSR ZEBRA | 369 | 850 | stability (30°) | 2739 | 850 | 7.6664e-06 | 0.00015947 | 0.0072724 | 4.5263 | 94.1533 | 0.0016772 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 27 | Built for 765 kV, operated at 400 kV (2023)
L0006 | Tirunelveli | Vellore | DHARAMAPURI | TUTICORIN-PS | Dharmapuri (Salem PS) 765/400 | Tuticorin PS 765/400 | 400 | 765 | AC | 2 | D/C | HEXA ACSR ZEBRA | 369 | 850 | stability (30°) | 2739 | 850 | 7.6664e-06 | 0.00015947 | 0.0072724 | 4.5263 | 94.1533 | 0.0016772 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 28 | Built for 765 kV, operated at 400 kV (2023)
L0052 | Trichy | Villupuram | NLC STG2 | PUGALUR-PG | NLC TPS-II 400/230 | Pugalur (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 198 | 1032 | thermal | 1032 | 1313 | 1.8e-05 | 0.0001923 | 0.00602 | 5.7024 | 60.9206 | 0.00074498 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 230
L0060 | Trichy | Villupuram | PUGALUR-PG | NLC STG2 EXP | Pugalur (PG) 400/230 | NLC TPS-II Expansion 400 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 200 | 1032 | thermal | 1032 | 1300 | 1.8e-05 | 0.0001923 | 0.00602 | 5.76 | 61.536 | 0.0007525 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 255
L0061 | Trichy | Villupuram | PUGALUR-PG | NNTPP | Pugalur (PG) 400/230 | New Neyveli TPS (NNTPP) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 258 | 1008 | stability (30°) | 1032 | 1008 | 1.8e-05 | 0.0001923 | 0.00602 | 7.4304 | 79.3814 | 0.00097073 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 256
L0085 | Trichy | Villupuram | TRICHY-PG | NAGAPATINAM-PS | Trichy (PG) 400/230 | Nagapattinam PS 765/400 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 159 | 1032 | thermal | 1032 | 1635 | 1.8e-05 | 0.0001923 | 0.00602 | 4.5792 | 48.9211 | 0.00059824 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 318
L0086 | Trichy | Villupuram | TRICHY-PG | NAGAPATINAM-PS | Trichy (PG) 400/230 | Nagapattinam PS 765/400 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 159 | 1032 | thermal | 1032 | 1635 | 1.8e-05 | 0.0001923 | 0.00602 | 4.5792 | 48.9211 | 0.00059824 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 319
L0125 | Trichy | Villupuram | PUGALUR-PG | ARIYALUR | Pugalur (PG) 400/230 | Ariyalur 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 184 | 1718 | stability (30°) | 2044 | 1718 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7017 | 46.5741 | 0.00084295 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 373
L0518 | Trichy | Villupuram | PUGALUR-PG | ARIYALUR | Pugalur (PG) 400/230 | Ariyalur 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 185 | 1708 | stability (30°) | 2044 | 1708 | 9.177e-06 | 0.0001582 | 0.00733 | 2.7164 | 46.8272 | 0.00084753 | TRUE | FALSE | TANTRANSCO | in service | SR Annual Compendium 2023-24 (SRLDC), Table 34 #19 (LILO), 10-02-2024
L0231 | Trichy | Villupuram | EACHANGADU | NLC TNEB | Eachangadu | Neyveli (TNEB) 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 45 | 260 | thermal | 260 | 1472 | 0.00014154 | 0.00075473 | 0.001552 | 10.1909 | 54.3405 | 4.3651e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 569
L0266 | Trichy | Villupuram | KADALANGUDY | NLC STG2 | Kadalangudy | NLC TPS-II 400/230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 92 | 260 | thermal | 260 | 720 | 0.00014154 | 0.00075473 | 0.001552 | 20.8347 | 111.0961 | 8.9241e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 604
L0267 | Trichy | Villupuram | KADALANGUDY | NLC TNEB | Kadalangudy | Neyveli (TNEB) 230 | 230 | 230 | AC | 1 | S/C | SINGLE ACSR ZEBRA | 77 | 270 | thermal | 270 | 863 | 0.00013175 | 0.00075208 | 0.0015411 | 16.2317 | 92.6557 | 7.4165e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 605
L0465 | Trichy | Villupuram | STCMS | PERMBALUR | ST-CMS Neyveli | Perambalur | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 64 | 260 | thermal | 260 | 1035 | 0.00014154 | 0.00075473 | 0.001552 | 14.4937 | 77.2842 | 6.2081e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 803
L0001 | Vellore | Andhra Pradesh | CUDDAPAH | THIRUVALAM-PG | Kadapa / Cuddapah (PG) 765/400 | Thiruvalam (PG) 765/400 | 765 | 765 | AC | 1 | D/C | HEXA ACSR ZEBRA | 245 | 4681 | stability (30°) | 5238 | 4681 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.82163 | 17.0912 | 0.0040731 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 5
L0002 | Vellore | Andhra Pradesh | CUDDAPAH | THIRUVALAM-PG | Kadapa / Cuddapah (PG) 765/400 | Thiruvalam (PG) 765/400 | 765 | 765 | AC | 2 | D/C | HEXA ACSR ZEBRA | 245 | 4681 | stability (30°) | 5238 | 4681 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.82163 | 17.0912 | 0.0040731 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 6
L0021 | Vellore | Andhra Pradesh | CHITTOOR | THIRUVALAM-PG | Chittoor 400/220 (AP) | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 21 | 2044 | thermal | 2044 | 15050 | 9.177e-06 | 0.0001582 | 0.00733 | 0.30835 | 5.3155 | 9.6206e-05 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 136
L0022 | Vellore | Andhra Pradesh | CHITTOOR | THIRUVALAM-PG | Chittoor 400/220 (AP) | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 21 | 2044 | thermal | 2044 | 15050 | 9.177e-06 | 0.0001582 | 0.00733 | 0.30835 | 5.3155 | 9.6206e-05 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 137
L0047 | Vellore | Andhra Pradesh | NELLORE-PG | THIRUVALAM-PG | Nellore (PG/PS) 400 | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 173 | 1827 | stability (30°) | 2044 | 1827 | 9.177e-06 | 0.0001582 | 0.00733 | 2.5402 | 43.7898 | 0.00079256 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 218
L0048 | Vellore | Andhra Pradesh | NELLORE-PG | THIRUVALAM-PG | Nellore (PG/PS) 400 | Thiruvalam (PG) 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 173 | 1827 | stability (30°) | 2044 | 1827 | 9.177e-06 | 0.0001582 | 0.00733 | 2.5402 | 43.7898 | 0.00079256 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 219
L0513 | Vellore | Andhra Pradesh | CHITTOOR 220/132 | THIRUVALAM 230/110 | Chittoor 220/132 (AP) | Thiruvalam (TN) 230/110 | 220 | 220 | AC | 1 | S/C | SINGLE ACSR KUNDAH + SINGLE ACSR DEER | 29 | 249 | thermal | 249 | 2090 | 0.0001547 | 0.0008249 | 0.00142 | 7.1781 | 38.2754 | 2.5737e-05 | TRUE | FALSE | APTRANSCO+TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 1190 |  | ACSR Deer not in parameter table: Zebra parameters used (likely overstates); mixed sections: weakest (highest-resistance) conductor used for whole line
L0007 | Vellore | Karnataka | TUMKUR-PG | DHARAMAPURI | Tumkur / Vasanthanarasapura (PG) 765/400 | Dharmapuri (Salem PS) 765/400 | 400 | 765 | AC | 1 | S/C | QUAD ACSR MOOSE | 245 | 1292 | stability (30°) | 2045 | 1292 | 9.167e-06 | 0.000158 | 0.00732 | 3.5935 | 61.936 | 0.0011209 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 31 | Built for 765 kV, operated at 400 kV (2023) | 4xACSR MOOSE not tabulated at 765 kV: 400 kV row used
L0008 | Vellore | Karnataka | TUMKUR-PG | DHARAMAPURI | Tumkur / Vasanthanarasapura (PG) 765/400 | Dharmapuri (Salem PS) 765/400 | 400 | 765 | AC | 2 | S/C | QUAD ACSR MOOSE | 222 | 1425 | stability (30°) | 2045 | 1425 | 9.167e-06 | 0.000158 | 0.00732 | 3.2561 | 56.1216 | 0.0010157 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 32 | Built for 765 kV, operated at 400 kV (2023) | 4xACSR MOOSE not tabulated at 765 kV: 400 kV row used
L0028 | Vellore | Karnataka | KOLAR-PG | HOSUR-PG | Kolar (PG) 400 / HVDC | Hosur (PG) 400/230 | 400 | 400 | AC | 1 | D/C | TWIN ACSR MOOSE | 69 | 1032 | thermal | 1032 | 3768 | 1.8e-05 | 0.0001923 | 0.00602 | 1.9872 | 21.2299 | 0.00025961 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 183
L0029 | Vellore | Karnataka | KOLAR-PG | HOSUR-PG | Kolar (PG) 400 / HVDC | Hosur (PG) 400/230 | 400 | 400 | AC | 2 | D/C | TWIN ACSR MOOSE | 69 | 1032 | thermal | 1032 | 3768 | 1.8e-05 | 0.0001923 | 0.00602 | 1.9872 | 21.2299 | 0.00025961 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 184
L0071 | Vellore | Karnataka | SOMANAHALLI-PG | DHARAMAPURI | Somanahalli (PG) 400/220 | Dharmapuri (Salem PS) 765/400 | 400 | 400 | AC | 1 | D/C | QUAD ACSR MOOSE | 121 | 2044 | thermal | 2044 | 2612 | 9.177e-06 | 0.0001582 | 0.00733 | 1.7767 | 30.6275 | 0.00055433 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 285
L0072 | Vellore | Karnataka | SOMANAHALLI-PG | DHARAMAPURI | Somanahalli (PG) 400/220 | Dharmapuri (Salem PS) 765/400 | 400 | 400 | AC | 2 | D/C | QUAD ACSR MOOSE | 121 | 2044 | thermal | 2044 | 2612 | 9.177e-06 | 0.0001582 | 0.00733 | 1.7767 | 30.6275 | 0.00055433 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 286
L0073 | Vellore | Karnataka | SOMANAHALLI-PG | HOSUR-PG | Somanahalli (PG) 400/220 | Hosur (PG) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 80 | 1015 | thermal | 1015 | 3012 | 1.862e-05 | 0.0002075 | 0.00555 | 2.3834 | 26.56 | 0.0002775 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 287
L0515 | Vellore | Karnataka | YERANDAHALLI | HOSUR | Yerandanahalli 220 | Hosur (TN) 230 | 220 | 220 | AC | 1 | S/C | SINGLE ACSR DRAKE | 40 | 231 | thermal | 231 | 1521 | 0.00018 | 0.000822 | 0.00141 | 11.52 | 52.608 | 3.525e-05 | TRUE | FALSE | KPTCL+TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 1620
L0529 | Vellore | Villupuram | THIRUVALAM-PG | ARIYALUR | Thiruvalam (PG) 765/400 | Ariyalur 765/400 | 765 | 765 | AC | 2 | D/C | HEXA ACSR ZEBRA | 173.56 | 5238 | thermal | 5238 | 6607 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.58205 | 12.1075 | 0.0028854 | TRUE | FALSE | TANTRANSCO | in service | SR Annual Compendium 2023-24 (SRLDC), Table 33 #22, 27-12-2023 | Same circuit also listed as #14 with 120 km on 20-10-2023 (likely partial charging); Thiruvalam end assumed to be the 765 kV (PG) bus
L0545 | Vellore | Villupuram | THIRUVALAM-PG | ARIYALUR | Thiruvalam (PG) 765/400 | Ariyalur 765/400 | 765 | 765 | AC | 1 | D/C | HEXA ACSR ZEBRA | 173.569 | 5238 | thermal | 5238 | 6607 | 2.096e-06 | 4.36e-05 | 0.0266 | 0.58208 | 12.1082 | 0.0028856 | TRUE | FALSE | TANTRANSCO | in service | SR Annual Compendium 2025-26 (SRLDC), Table 57, charged 03-12-2025 | Thiruvalam end assumed to be the existing 765 kV (PG) bus; 240 MVAr line reactor at Ariyalur
L0003 | Vellore | Villupuram | DHARAMAPURI | NAGAPATINAM-PS | Dharmapuri (Salem PS) 765/400 | Nagapattinam PS 765/400 | 400 | 765 | AC | 1 | D/C | HEXA ACSR ZEBRA | 204 | 1537 | stability (30°) | 2739 | 1537 | 7.6664e-06 | 0.00015947 | 0.0072724 | 2.5023 | 52.0523 | 0.00092723 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 25 | Built for 765 kV, operated at 400 kV (2023)
L0004 | Vellore | Villupuram | DHARAMAPURI | NAGAPATINAM-PS | Dharmapuri (Salem PS) 765/400 | Nagapattinam PS 765/400 | 400 | 765 | AC | 2 | D/C | HEXA ACSR ZEBRA | 204 | 1537 | stability (30°) | 2739 | 1537 | 7.6664e-06 | 0.00015947 | 0.0072724 | 2.5023 | 52.0523 | 0.00092723 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 26 | Built for 765 kV, operated at 400 kV (2023)
L0199 | Vellore | Villupuram | ARANI | SINGARAPET | Arani | Singarapettai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 98 | 260 | thermal | 260 | 676 | 0.00014154 | 0.00075473 | 0.001552 | 22.1935 | 118.3415 | 9.5062e-05 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 537
L0454 | Vellore | Villupuram | SINGARAPET | THIRUVANAMALAI | Singarapettai | Tiruvannamalai | 230 | 230 | AC | 1 | S/C | SINGLE ACSR KUNDAH | 111 | 260 | thermal | 260 | 597 | 0.00014154 | 0.00075473 | 0.001552 | 25.1376 | 134.0399 | 0.00010767 | TRUE | FALSE | TANTRANSCO | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 792
L0055 | Villupuram | Puducherry | NNTPP | PONDY | New Neyveli TPS (NNTPP) 400/230 | Pondicherry (PG) 400/230 | 400 | 400 | AC | 1 | S/C | TWIN ACSR MOOSE | 66 | 1015 | thermal | 1015 | 3651 | 1.862e-05 | 0.0002075 | 0.00555 | 1.9663 | 21.912 | 0.00022894 | TRUE | FALSE | PGCIL | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 233
L0155 | Villupuram | Puducherry | NLC STG2 | KARAIKAL | NLC TPS-II 400/230 | Karaikal 230 | 230 | 230 | AC | 1 | D/C | SINGLE ACSR KUNDAH | 101.6 | 260 | thermal | 260 |  | 0.00014154 | 0.00075473 | 0.001552 | 23.0088 | 122.6887 | 9.8554e-05 | TRUE | TRUE | PONDY | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 493 |  | S/C parameters used (D/C not tabulated); length not available – thermal limit only
L0156 | Villupuram | Puducherry | NLC STG2 | VILLIANUR | NLC TPS-II 400/230 | Villianur 230 | 230 | 230 | AC | 1 | D/C | SINGLE ACSR KUNDAH | 63 | 260 | thermal | 260 | 1052 | 0.00014154 | 0.00075473 | 0.001552 | 14.2673 | 76.0767 | 6.1111e-05 | TRUE | FALSE | PONDY | in service | SRLDC Compendium of SR Transmission Elements 2023 (via CTUIL), row 494 |  | S/C parameters used (D/C not tabulated)

## network
name | _multi_invest | pypsa_version | srid
Tamil Nadu 9 balancing areas – inter-area transmission, end FY2025-26 | 0 | 1.4.0 | 4326

## crs
Key | Value
_crs | GEOGCRS["WGS 84",ENSEMBLE["World Geodetic System 1984 ensemble",MEMBER["World Geodetic System 1984 (Transit)"],MEMBER["World Geodetic System 1984 (G730)"],MEMBER["World Geodetic System 1984 (G873)"],MEMBER["World Geodetic System 1984 (G1150)"],MEMBER["World Geodetic System 1984 (G1674)"],MEMBER["World Geodetic System 1984 (G1762)"],MEMBER["World Geodetic System 1984 (G2139)"],MEMBER["World Geodetic System 1984 (G2296)"],ELLIPSOID["WGS 84",6378137,298.257223563,LENGTHUNIT["metre",1]],ENSEMBLEACCURACY[2.0]],PRIMEM["Greenwich",0,ANGLEUNIT["degree",0.0174532925199433]],CS[ellipsoidal,2],AXIS["geodetic latitude (Lat)",north,ORDER[1],ANGLEUNIT["degree",0.0174532925199433]],AXIS["geodetic longitude (Lon)",east,ORDER[2],ANGLEUNIT["degree",0.0174532925199433]],USAGE[SCOPE["Horizontal component of 3D system."],AREA["World."],BBOX[-90,-180,90,180]],ID["EPSG",4326]]

## meta
Key | Value

## snapshots
| snapshot | objective | stores | generators
0 | now | 1 | 1 | 1